## Cluster_Variables
Cluster No | Cluster Name | Variable Group | Key Tags / Signals | Role in Model | Depends On (Clusters) | Feeds / Used By
1 | Cluster 1 – Load / Flow / Mass Balance | Demand / output | Unit load; Total main steam flow (A/B) | Defines boiler production and demand reference for all clusters. |  | Clusters 2–12; Boiler KPI dashboard
1 | Cluster 1 – Load / Flow / Mass Balance | Water-side response | Feedwater flow to FCS; Spray-water flow; Blowdown where available | Establishes water–steam balance and deviation against steam generation. |  | Efficiency, heat-rate and mass-balance KPIs
1 | Cluster 1 – Load / Flow / Mass Balance | Combustion air totals | Total PA flow; Total SA flow; Total TA flow | Defines total combustion air vs load and steam; supports excess-air and draft logic. |  | Clusters 3, 5, 7, 8, 9, 10, 11
1 | Cluster 1 – Load / Flow / Mass Balance | Side / distribution indicators | PA/SA/TA A/B side splits; side balance indices | Detects air maldistribution and measurement drift at boiler inlet. |  | Air distribution and combustion-stability KPIs
2 | Cluster 2 – PA Fan Performance | Operating demand | Validated load; Total main steam flow (Cluster 1) | Provides demand context for PA duty and fan baseline. | Cluster 1 | Clusters 3, 5, 7, 9, 11; PA fan KPIs
2 | Cluster 2 – PA Fan Performance | PA fan head & flow | PA Fan A/B head; PA Fan A/B flow | Captures PA fan delivered performance vs duty. | Cluster 1 | Draft balance, combustion air and mill/feeder clusters
2 | Cluster 2 – PA Fan Performance | Control position | PA Fan A/B IGV feedback | Represents inlet-guide-vane control response vs PA duty. | Cluster 1 | Fan control health and auxiliary-power KPIs
2 | Cluster 2 – PA Fan Performance | Electrical & mechanical response | PA Fan A/B VFD current; PA Fan A/B RPM | Defines motor loading and speed effort for given demand. | Cluster 1 | Fan health (FHI), performance (FPI) and draft clusters
3 | Cluster 3 – Draft System PA–SA–ID Balance | Demand / output | Validated load; Total main steam flow (Cluster 1) | Primary demand reference for draft-system duty. | Cluster 1 | Draft safety, furnace-pressure and air/gas balance KPIs
3 | Cluster 3 – Draft System PA–SA–ID Balance | Primary air system | PA Fan A/B RPM & current; Total PA flow; PA head | Relates PA fan effort to delivered primary air. | Clusters 1, 2 | Combustion, mill/feeder and PA header clusters
3 | Cluster 3 – Draft System PA–SA–ID Balance | Secondary air system | SA Fan A/B speed & current; SA Flow-A/B; SA head | Relates SA fan effort to delivered secondary air. | Clusters 1, 4 | SA distribution (Cluster 8), combustion and draft KPIs
3 | Cluster 3 – Draft System PA–SA–ID Balance | Induced draft system | ID Fan A/B speed & current; ID head; ID flow | Represents flue-gas extraction effort vs incoming air and demand. | Clusters 1, 7 | Flue-gas path clusters (9, 11) and furnace-draft KPIs
3 | Cluster 3 – Draft System PA–SA–ID Balance | Supporting air flow | TA Flow-A/B (where applicable) | Completes total incoming combustion-air relationship. | Cluster 1 | Combustion balance, bed and gas-temperature clusters
4 | Cluster 4 – SA Fan Performance | Operating demand | Validated load; Total main steam flow (Cluster 1) | Defines expected SA duty for each load band. | Cluster 1 | Cluster 3, Cluster 8; SA fan KPIs
4 | Cluster 4 – SA Fan Performance | SA fan head & flow | SA Fan A/B head; SA Fan A/B flow | Fan-performance indicators for secondary-air delivery. | Cluster 1 | Combustion air, SA distribution and draft clusters
4 | Cluster 4 – SA Fan Performance | Control position | SA Fan A/B IGV feedback | Represents IGV control response for SA duty. | Cluster 1 | Fan control health and auxiliary-power KPIs
4 | Cluster 4 – SA Fan Performance | Electrical & mechanical response | SA Fan A/B VFD current; SA Fan A/B RPM | Motor and speed effort associated with SA operating point. | Cluster 1 | Cluster 3, 8, 11; FPI/FHI fan indices
5 | Cluster 5 – PA Header & Total Flow | Demand reference | Steam Flow-A; Steam Flow-B (validated) | Defines expected PA demand and load bands. | Cluster 1 | Startup/low-load combustion and PA fan clusters
5 | Cluster 5 – PA Header & Total Flow | Primary key – Total PA | Total PA flow | Main PA output indicator, benchmarked against steam demand. | Clusters 1, 2 | Combustion, bed and air-distribution clusters
5 | Cluster 5 – PA Header & Total Flow | HGG branch-A | PA flow to HGG-A (1); PA flow to HGG-A (2) | Validates branch-A delivery and redundant flow readings during startup. | Cluster 1 | Startup diagnostics and air/fuel distribution analysis
5 | Cluster 5 – PA Header & Total Flow | HGG branch-B | PA flow to HGG-B (1); PA flow to HGG-B (2) | Validates branch-B delivery and redundant readings. | Cluster 1 | Startup diagnostics and A/B distribution KPIs
6 | Cluster 6 – Gas Temperature Profile | Demand / output | Load; Total main steam flow; Unit generation | Defines expected gas-path temperature duty. | Cluster 1 | Gas temperature, back-end loss and heat-transfer KPIs
6 | Cluster 6 – Gas Temperature Profile | Fuel input | Fuel flow; coal flow; fuel GCV/NCV; moisture; ash | Explains changes in heat release, adiabatic temperature and fouling tendency. |  | Combustion optimisation and fuel-impact analytics
6 | Cluster 6 – Gas Temperature Profile | Combustion / air | PA/SA/TA flows; O2; excess air; windbox/air-header pressure | Supports interpretation of high/low gas temperatures and combustion quality. | Clusters 1, 3, 8 | Combustion clusters, APH and stack-loss modules
6 | Cluster 6 – Gas Temperature Profile | Furnace zone | Furnace temperature; FEGT; furnace-exit gas temperatures (L/R/Avg) | First temperature reference after combustion; sensitive to furnace absorption. | Cluster 1 | Superheater, bed and draft clusters
6 | Cluster 6 – Gas Temperature Profile | SH/RH zone | Gas temperature before/after platen SH, final SH, reheater | Captures heat absorption and temperature drop through high-temperature surfaces. | Clusters 1, 12 | Superheater and steam-temperature KPIs
6 | Cluster 6 – Gas Temperature Profile | Economiser zone | Economiser inlet/outlet gas temperature; feedwater temperatures/flow | Validates economiser heat pickup and gas-side fouling. | Clusters 1, 9, 11 | Eco/APH performance and efficiency KPIs
6 | Cluster 6 – Gas Temperature Profile | APH & stack | APH gas inlet/outlet temperature; air inlet/outlet temperature; stack temperature | Represents final heat recovery and stack loss tendency. | Clusters 1, 11 | Stack temperature, APH performance and loss analysis
7 | Cluster 7 – ID Fan Performance | Operating demand | Validated load; Total main steam flow | Defines expected ID duty for gas extraction. | Cluster 1 | Cluster 3, 9, 11; draft and exhaust KPIs
7 | Cluster 7 – ID Fan Performance | Total air / gas flow | Combination of Total PA, SA, TA flows | Relates ID duty to total incoming air and resulting gas flow. | Cluster 1, 3 | Flue-gas path and draft balance clusters
7 | Cluster 7 – ID Fan Performance | ID fan head & flow | ID Fan A/B head; ID Fan A/B flow | Fan-performance indicators for flue-gas movement. | Cluster 1 | ESP/ECO/APH clusters and stack-loss KPIs
7 | Cluster 7 – ID Fan Performance | Control position | ID Fan A/B IDC feedback | Represents IGV/IDC control response for ID duty. | Cluster 1 | Fan control and draft stability KPIs
7 | Cluster 7 – ID Fan Performance | Electrical & mechanical response | ID Fan A/B VFD current; ID Fan A/B RPM | Motor loading and speed effort vs gas-path resistance. | Cluster 1 | Auxiliary-power, reliability and draft clusters
8 | Cluster 8 – SA Air Distribution | Operating demand | Validated Steam Flow-A/B | Defines expected combustion duty and SA load band. | Cluster 1 | Combustion, bed and gas-temperature clusters
8 | Cluster 8 – SA Air Distribution | Upstream pressure | SA pressure to APH (A/B) | Pressure delivered toward/through APH on each side. | Clusters 4, 11 | APH, SA fan and draft clusters
8 | Cluster 8 – SA Air Distribution | Furnace delivery pressure | SA pressure at furnace inlet; SA pressure to furnace | Represents usable SA pressure reaching furnace. | Cluster 3 | Combustion and furnace-draft KPIs
8 | Cluster 8 – SA Air Distribution | Temperature delivery | SA temperature to furnace (1/2); Air-box temperature A/B | Represents SA heat pickup and side-wise thermal distribution. | Clusters 6, 11 | Combustion quality, APH performance and bed clusters
8 | Cluster 8 – SA Air Distribution | Flow delivery | SA Flow-A; SA Flow-B | Measures secondary-air quantity per side and total SA flow. | Clusters 1, 4 | Draft balance, combustion and SA fan clusters
9 | Cluster 9 – Flue Gas Path / ESP / Economiser-1 | Operating demand | Validated Steam Flow-A/B | Defines expected gas generation and heat-release duty. | Cluster 1 | ESP/ECO/APH and stack-related KPIs
9 | Cluster 9 – Flue Gas Path / ESP / Economiser-1 | ESP temperature | FG temperature before ESP; FG temperature after ESP | Measures thermal condition across ESP section. | Clusters 6, 7 | ESP performance and gas-path diagnostics
9 | Cluster 9 – Flue Gas Path / ESP / Economiser-1 | ESP pressure | Pressure before ESP; Pressure after ESP | Measures gas-path pressure loss across ESP. | Cluster 7 | Draft-loss and restriction detection
9 | Cluster 9 – Flue Gas Path / ESP / Economiser-1 | Eco-1 inlet | FG pressure to Eco-1 inlet; FG temperature Eco-1 inlet | Defines inlet gas condition for Economiser-1. | Clusters 1, 6 | Economiser-1 heat-pickup and draft analysis
9 | Cluster 9 – Flue Gas Path / ESP / Economiser-1 | Eco-1 outlet | Gas temperature Eco-1 outlet; Gas pressure Eco-1 outlet; O2 Eco-1 outlet (site-specific) | Defines outlet condition and heat-pickup across Eco-1. | Clusters 6, 8 | Eco-1 performance and downstream APH clusters
9 | Cluster 9 – Flue Gas Path / ESP / Economiser-1 | Stack approach | FG temperature before stack | Provides downstream exhaust-temperature evidence. | Clusters 6, 11 | Stack temperature and back-end loss KPIs
10 | Cluster 10 – Bed Temperature Monitoring | Demand / output | Validated Steam Flow-A/B; Load | Defines combustion duty and bed temperature bands. | Cluster 1 | Combustion, safety and bed-health KPIs
10 | Cluster 10 – Bed Temperature Monitoring | Fuel / heat input | Fuel flow; fuel GCV/moisture/ash where available | Explains bed temperature drift and response to fuel disturbance. |  | Fuel-impact and combustion optimisation modules
10 | Cluster 10 – Bed Temperature Monitoring | Combustion air | Total PA flow; SA Flow-A/B; TA Flow-A/B; PA/SA pressures and temperatures | Supports diagnosis of air sufficiency and fluidization adequacy. | Clusters 1, 3, 5, 8 | Bed-fluidization, combustion and draft clusters
10 | Cluster 10 – Bed Temperature Monitoring | Bed inventory / fluidization | Bed height (bed pressure drop); furnace pressure below screen A/B/C; below-screen temperatures | Indicates bed inventory, pressure distribution and fluidization health. | Cluster 3 | Combustion and bed-stability KPIs
10 | Cluster 10 – Bed Temperature Monitoring | Bed temperature profile | Bed Temp Avg; Bed Temp A–F | Primary indicators for average bed condition and hot/cold zones. | Cluster 6 | Hot-spot detection and agglomeration-risk analysis
10 | Cluster 10 – Bed Temperature Monitoring | Ash circulation / loop seal | Cyclone-A/B ash outlet temperatures; Syphon A/B exit temperatures | Tracks recirculated ash temperature and loop-seal behaviour. |  | Ash recirculation, cyclone health and bed-stability KPIs
11 | Cluster 11 – Airheater Performance Monitoring | Demand / output | Validated Steam Flow-A/B; Load | Defines APH heat-transfer requirement per load band. | Cluster 1 | Stack-loss, auxiliary-power and APH-health KPIs
11 | Cluster 11 – Airheater Performance Monitoring | Air-side inlet/output | PA/SA temperature before APH; PA/SA temperature after APH; Air-box temperature A/B; SA temperature to furnace | Measures air-side temperature pickup and combustion-air heating. | Clusters 6, 8 | Combustion, SA distribution and APH performance KPIs
11 | Cluster 11 – Airheater Performance Monitoring | Air-side pressure / flow | PA pressure to APH; SA pressure to APH A/B; Total PA flow; SA Flow-A/B; TA Flow-A/B; PA/SA fan current/speed | Detects air-side restriction, leakage, maldistribution and increased fan effort. | Clusters 2, 4, 7 | Draft-loss, auxiliary-power and fan-health KPIs
11 | Cluster 11 – Airheater Performance Monitoring | Gas-side temperature | FG temperature at Eco outlet / APH inlet; FG temperature before ESP; FG temperature after APH | Measures gas-side cooling and heat-transfer deterioration. | Clusters 6, 9 | Back-end loss and APH fouling indicators
11 | Cluster 11 – Airheater Performance Monitoring | Gas-side pressure / draft | FG pressure before/after APH or nearby draft taps; FG pressure before/after ESP; ID fan speed/current | Detects gas-side choking, fouling and draft-loss increase. | Clusters 3, 7, 9 | Draft and back-end performance KPIs
11 | Cluster 11 – Airheater Performance Monitoring | Leakage / combustion cross-check | O2 LHS/RHS; excess air; furnace pressure; ID fan response | Supports APH leakage and false-air ingress diagnosis. | Clusters 3, 6, 9 | Combustion and leakage-monitoring KPIs
12 | Cluster 12 – Superheater Performance Monitoring | Demand / output | Validated Steam Flow-A/B; Load | Defines superheater steam duty and expected outlet temperature band. | Cluster 1 | Steam-temperature, tube-health and heat-rate KPIs
12 | Cluster 12 – Superheater Performance Monitoring | Pressure reference | Drum pressure; SH-3 outlet steam pressure A/B | Defines pressure level and pressure-drop behaviour across SH circuit. |  | Pressure-drop and tube-stress analysis
12 | Cluster 12 – Superheater Performance Monitoring | SH-1 temperature profile | SH-1 inlet steam temperature A/B; SH-1 outlet steam temperature A/B | Identifies first-stage heat pickup and side-wise imbalance. | Cluster 6 | Superheater health and gas-temperature clusters
12 | Cluster 12 – Superheater Performance Monitoring | SH-2 temperature profile | SH-2 inlet steam temperature (where available); SH-2 outlet steam temperature A/B | Tracks intermediate heat absorption and stage temperature rise. | Cluster 6 | Superheater performance indices
12 | Cluster 12 – Superheater Performance Monitoring | SH-3 / final temperature profile | SH-3 inlet steam temperature A/B; SH-3 outlet steam temperature A/B | Primary final superheater temperature output and tube-risk zone. | Clusters 6, 11 | Final steam-temperature and tube-health KPIs
12 | Cluster 12 – Superheater Performance Monitoring | Spray / attemperator control | Spray valve feedback; spray flow; attemperator inlet/outlet temperature (where available) | Diagnoses over-spray, under-spray and spray-control abnormality. |  | Temperature-control and stability KPIs
12 | Cluster 12 – Superheater Performance Monitoring | Combustion / gas-side dependency | Fuel flow; Total air flow; O2 LHS/RHS; bed temperature or FEGT; sootblower status | Supports diagnosis of gas-side heat release, fouling and imbalance. | Clusters 3, 6, 10 | Cross-cluster RCA and superheater health