# Flow Chart – Cluster 1 to Cluster 3 (Boiler KPI Validation)

This document provides a structured flow chart for the first three boiler KPI validation clusters: Cluster 1 (Load / Flow / Mass Balance), Cluster 2 (PA Fan Performance), and Cluster 3 (Draft System Balance). It is intended as a starting point for digital MVP implementation and can be further refined into graphical process diagrams in Word, Visio, or BPMN tools.

# Relationship Between Cluster 1 and Cluster 2

| Cluster | Primary role | Main output / hand-off |
| --- | --- | --- |
| Cluster 1 Load / Flow / Mass Balance | Validate demand reference, water–steam balance, total combustion air and side distribution. | Validated load / steam demand, balance residuals and quality/status flags. |
| Cluster 2 PA Fan Performance | Evaluate Fan-A/B control, speed and electrical response against validated demand. | Predicted vs actual PA fan variables, residuals, A/B imbalance and fan health status. |

## Cluster 1 – Load / Flow / Mass Balance

Start: Acquire aligned snapshot for current timestamp – load, main steam flow (A/B), feedwater flow, spray-water flows, total combustion air (PA + SA + TA), quality flags, and operating state.

Validate demand reference – compare total main steam flow against load within user-defined bands for each load range; if disagreement exceeds limits, mark demand as invalid and restrict downstream health alarms.

Compute water–steam balance deviation – evaluate (Feedwater Flow − Total Main Steam Flow) relative to Total Main Steam Flow and check against acceptable deviation limits per load band.

Validate combustion-air vs load and steam – aggregate PA, SA and TA flows, calculate total combustion air, and confirm that air delivery follows historically healthy envelopes for the current load band.

Evaluate PA/SA/TA split and A/B side balances – derive air-share indicators and side differences to detect maldistribution or tag drift.

Decision: Mass-balance healthy? If demand reference, water–steam deviation and air–load relationships are all within limits, set Cluster 1 Status = Healthy; otherwise set Status = Warning/Alarm with specific residuals.

Output: Validated demand (load, total steam), mass-balance residuals and status flags for use by Cluster 2 (PA fan duty) and Cluster 3 (draft-system duty), and tag boiler KPIs with validation status.

# . Flow Chart — Cluster 1: Load / Flow / Mass Balance

INPUT DATA Load • Main steam flow A/B • Feedwater flow • Spray-water flow • PA/SA/TA flows • Quality flags • Operating state

↓

Synchronize timestamp and validate tag quality Check missing, frozen, spiky, impossible or bad-quality values

↓

Validate demand reference Compare load with total main steam flow within load-band-specific healthy limits

↓

Calculate water–steam balance residual (Feedwater Flow − Total Main Steam Flow) / Total Main Steam Flow

↓

Validate total combustion air Aggregate PA + SA + TA and compare against load / steam healthy envelope

↓

Evaluate distribution Check PA/SA/TA split and A/B side imbalance for maldistribution or measurement drift

↓

| DECISION: Are demand, balance and air relationships within limits? |  |
| --- | --- |
| YES — Set Cluster 1 = HEALTHY | NO — Set WARNING / ALARM and identify failed residuals |

↓

OUTPUT / HAND-OFF Validated load and steam demand • Mass-balance residuals • Air-distribution indicators • Data-quality and status flags → Cluster 2 and downstream KPI modules

## Cluster 2 – PA Fan Performance

Start: Receive Cluster 1 validated demand (load, total steam) together with PA fan-A/B tags – RPM, inlet-guide-vane (IGV) feedback, VFD motor current, PA head and PA flow, plus fan configuration.

Assign demand context and fan configuration – map the snapshot to load band and operating mode (steady, ramp, low load, changeover) and identify whether single-fan, dual-fan or changeover operation applies.

Compute expected PA fan variables – using historical training, predict normal RPM, IGV feedback and motor current for each fan at the prevailing demand and companion-fan condition.

Calculate residuals and A/B differences – for each PA fan variable (RPM, IGV, current, flow), compute Fan Residual = Actual − Predicted, normalized residual (%) and, where both fans run, A/B imbalance metrics.

Decision: PA fan response healthy? If residuals for RPM, IGV and current are within load-band-specific limits and A/B imbalances remain inside the historical relative-difference range, set Cluster 2 Status = Healthy; otherwise set Status = Warning/Alarm with detailed deviation reasons.

Output: Per-fan residuals, A/B imbalance and health flags to Cluster 3 for draft-balance interpretation, and to PA-related KPI modules (e.g. fan operating KPI and auxiliary-power KPIs).

# Flow Chart — Cluster 2: PA Fan Performance

INPUT DATA Validated demand from Cluster 1 • PA Fan-A/B RPM • IGV feedback • VFD current • Head • Flow • Fan operating configuration

↓

Confirm input validity and operating mode Apply Cluster 1 status; classify steady load, low load, ramp, single-fan, dual-fan or changeover operation

↓

Select applicable healthy model Use load band, steam demand and companion-fan condition to select the normal operating relationship

↓

Predict expected PA fan response Expected RPM • IGV feedback • Motor current • Head / flow, where available

↓

Calculate performance indicators Residual = Actual − Predicted • Normalized residual (%) • Fan-A/B relative imbalance

↓

Apply persistence and data-quality logic Separate short spikes / transients from sustained deviation

↓

| DECISION: Are residuals and A/B imbalance within accepted limits? |  |
| --- | --- |
| YES — Set Cluster 2 = HEALTHY | NO — Set WARNING / ALARM with deviation reason |

↓

OUTPUT / HAND-OFF Actual vs predicted trends • Per-fan residuals • A/B imbalance • Health flags → Draft System Balance, fan KPI and auxiliary-power modules

## Cluster 3 – Draft System PA–SA–ID Balance

Start: Receive Cluster 1 (validated demand and mass balance) and Cluster 2 (PA fan health outputs), together with SA and ID fan tags – speeds, currents, heads – and SA/TA flows, fuel-flow where measured, and operating mode/fan configuration.

Compute combined air and gas flows – derive Total Secondary Air (SA-A + SA-B), Total Tertiary Air (TA-A + TA-B where applicable), Total Combustion Air (Total PA + Total SA + Total TA) and an estimated Total Gas Flow based on combustion air and fuel-flow.

Apply expected PA/SA/ID relationships – use trained relationships to determine expected PA/SA flows and ID response as functions of load or steam flow, fan speed and fan current.

Evaluate draft-balance relationships – check load/steam vs PA flow, load/steam vs SA flow, PA/SA ratios, load vs PA/SA/ID currents, PA/SA speed–current vs flow, incoming-air vs ID response and A/B normalized responses for each system.

Compute residuals and imbalance metrics – calculate Fan Variable Residuals (Actual − Predicted), normalized residual (%) and A/B imbalance (%) for PA, SA and ID systems across valid load bands and configurations.

Decision: Draft-system balance healthy? Accept values when residuals remain within user-defined limits and persistence time; flag Warning/Alarm when limits are exceeded, interpreting specific patterns such as high effort/normal flow, low flow/normal effort, high ID effort without matching demand, or ID lag behind rising PA/SA duty.

Output: Publish actual, predicted and normal-band values for PA/SA flows and PA/SA/ID fan speeds/currents, together with residuals, persistence, A/B imbalance and an overall draft-balance status for use by draft/safety KPIs and boiler operating dashboards.

# .

# Flow Chart Cluster 3 — Draft System PA–SA–ID Balance

Boiler KPI Validation Flow Chart

INPUT / UPSTREAM VALIDATION Cluster 1: validated load, steam flow, total PA/SA/TA flow and mass-balance status • Cluster 2: PA Fan-A/B health outputs • SA and ID fan speed/current/head/flow • Fuel flow and operating configuration, where available

↓

Synchronize data and validate tag quality Check timestamp alignment, missing/frozen/spiky values, engineering units, operating state and fan availability

↓

Classify operating condition and fan configuration Steady load • Low load • Ramp-up / ramp-down • Single-/dual-fan operation • Fan changeover

↓

Calculate combined air and gas-flow indicators Total SA = SA-A + SA-B • Total TA = TA-A + TA-B • Total Combustion Air = PA + SA + TA • Gas-flow proxy from combustion air and fuel, where available

↓

Generate expected draft-system response from healthy historical relationships Expected PA/SA flows and expected PA/SA/ID speed, current, head and flow for the applicable demand and configuration

↓

Evaluate coordination and balance relationships Load/steam vs PA and SA flow • PA/SA ratio • Incoming air vs ID response • Speed/current vs delivered flow • A/B normalized response for PA, SA and ID systems

↓

Calculate validation indicators Residual = Actual − Predicted • Normalized residual (%) • Fan-A/B imbalance (%) • Persistence of deviation

↓

| DECISION: Is the PA–SA–ID draft-system relationship within accepted residual, imbalance and persistence limits? |  |
| --- | --- |
| YES — Set Cluster 3 = HEALTHY | NO — Set WARNING / ALARM and identify the abnormal relationship |

↓

OUTPUT / HAND-OFF Actual, predicted and normal-band values • PA/SA/ID residuals • A/B imbalance • Persistence • Overall draft-balance status → Furnace draft safety, air/gas balance, fan KPI and boiler dashboard modules