# Cluster 1 - Load-Flow Mass Balance

Training data relationships, validation logic and performance checking

| OBJECTIVE | Establish the normal coordination between boiler load, main steam generation, feedwater supply and combustion-air delivery, so that developing mass-balance deviations are detected early. |
| --- | --- |

# Scope and Variables

Cluster 1 is the operating-reference cluster for the boiler operation. It links the process demand represented by load with the flows required to sustain that demand. The model should learn the combined response of the variables, not treat each tag as an isolated measurement and will try to corelate relationship between variables.

| Indicator | Calculation / relationship | Primary interpretation |
| --- | --- | --- |
| Demand / output | Load; Steam Flow-A; Steam Flow-B | Defines boiler production and steam-side response. |
| Water side | Feedwater Flow to FCS, Spray Water Flow |  |
| Combustion air | Total PA Flow; SA Flow-A/B; TA Flow-A/B | Supports fuel transport, fluidization and combustion. |
| Note: Tags may vary for different plants and will require project specific adjustment. |  |  |

# Process Relationship to be Learned

LOAD DEMAND  ->  FIRING REQUIREMENT  ->  COMBUSTION AIR  ->  STEAM GENERATION  ->  FEEDWATER RESPONSE

Load not available

## Load and Main Steam Flow

Load is the principal operating reference; total main steam flow is the direct process response. During stable operation, the relationship should be strong and repeatable within each load band. Load band is a user Input to be the Input Parameters

For Example, for a 100 TPH Boiler can be divided in 4 load ranges depending on operation philosophy and plants historical data

90 – 100 T.P.H

75 – 90 T.P.H

60 – 75 T.P.H

40 – 60 T.P.H

In these cases, there are two measurement points.

Total Main Steam Flow = (Steam Flow-A + Steam Flow-B)/2 (If Measurement Points in Series) (1) Total Main Seam Flow = (Steam Flow-A + Steam Flow-B)/1 (If Measurement Points in Parallel)

A sustained load-to-steam mismatch may indicate signal drift, abnormal steam consumption.

In case of Eq 1 Corelate both readings acceptable variation 3% (Example User Input)

In case two readings differ Correlate with Feed Flow

Steam Flow Error = f(Feed Water Flow, Spray Flow) (1) Total Main Seam Flow = Feed Water Flow + Steam Flow Error

## Feedwater and Steam Balance

At steady conditions, feedwater flow should broadly balance steam generation after allowing for drum inventory change, blowdown, spray-water contribution and instrument uncertainty. Normal deviation is acceptable but variation in imbalance is c

Water-Steam Balance Deviation (%) = (Feedwater Flow - Total Main Steam Flow) / Total Main Steam Flow x 100

- There is a relationship between Steam Flow, Feed Water Flow and Load. In case Steam Flow are Feed Flow are not matching both values should be correlated with Load. The value matching with load should be considered and other will be corrected.

- #No Load tag available

# Airflow Relationships and Derived Indicators

Primary, secondary and tertiary airflows should move with firing demand, but the relationship may be nonlinear because of fuel quality, excess-air setting, bed condition, load range and operating configuration. The training objective is therefore a load-dependent operating envelope rather than one fixed ratio.

| Total Secondary Air = SA Flow-A + SA Flow-B |  |  |
| --- | --- | --- |
| Total Tertiary Air = TA Flow-A + TA Flow-B |  |  |
| Total Combustion Air = Total PA + Total SA + Total TA |  |  |
| Indicator | Calculation / relationship | Primary interpretation |  |
| Total air vs load | Expected airflow envelope at each load range. | Overall shortage or excess relative to normal demand. |  |
| PA share | Total PA / Total Combustion Air | Change in primary-air contribution. |  |
| SA share | Total SA / Total Combustion Air | Change in secondary-air contribution. |  |
| TA share | Total TA / Total Combustion Air | Change in tertiary-air contribution. |  |
| A/B balance | Side difference / side average x 100 | Developing side maldistribution or measurement drift. |  |

Create a relationship between Steam Flow and Air Flow from historical data to check variation from expected value.

Air Flow (Expected) = f (Steam Flow) (2) Air Flow (Expected) = f (Steam Flow, PA /SA distrubtion, 02%) (3)

Air Flow is dependent on few parameters like Excess Air, Load, PA /SA distribution, O2 % not part of Cluster 1 will be developed in different cluster. As per equation (1) Air Flow will have range in case incoming values goes outside the range the model will flag alarm and will further investigate in a different cluster.

## A/B-Side Balance

Steam, secondary-air and tertiary-air side balances should be evaluated against the historically healthy baseline. A perfectly equal split should not be assumed it will be an ideal condition realistically not possible. Trend movement is often more informative than the absolute difference.

SA Side Deviation (%) = (SA-A - SA-B) / [(SA-A + SA-B) / 2] x 100

# Preparation for Training Data

Synchronize all tags to a common timestamp and sampling interval.

Classify operating state: steady load, ramp-up, ramp-down, low load, start-up, shutdown and equipment changeover.

Exclude bad quality, frozen, missing, impossible or maintenance-affected measurements. It is better not to  replace long gaps with interpolation.

Cover the full normal load range and normal equipment combinations. Do not allow one load band to dominate the training set.

Retain valid process variation caused by normal fuel and control behaviour; remove only technically invalid data.

Important: Start-up, shutdown, trips and known instrument-fault periods should not be mixed with healthy steady-state training data if adequate data are available create separate operating-state model for different transient condition.

# Data Validation Framework

| Validation layer | Minimum checks |
| --- | --- |
| Tag level | Missing data, frozen values, spikes, noise, negative/impossible values, scaling and unit errors. |
| Relationship level | Load-steam, feedwater-steam, total-air-load, PA/SA/TA distribution, and A/B balance consistency. |
| Operating-state level | Separate limits for steady operation, ramps, low load, equipment changeover, start-up and shutdown. |

# Performance Checking

For each variable, the trained normal-behavior model should generate an expected value and a load-dependent normal band. Performance is checked through the residual between measured and predicted values, together with deviation duration and corroboration from related variables.

Residual = Actual Value - Predicted Value

Create an accepted user defined residuals for each measurement points based on primary and secondary key.Validate an incoming value if the residual is within acceptable limit.

## Recommended Dashboard Outputs

- Actual value predicted value and normal operating band.

- Absolute residual and percentage residual, with model confidence and data-quality status.

- Water-steam balance deviation and duration outside the accepted envelope.

- Total combustion air versus load, with PA/SA/TA percentage distribution.

- Steam-flow, SA-flow and TA-flow A/B side-balance trends.

- Operating-state label so that steady-state and transient limits are not mixed.

Conclusion. Cluster 1 should function as the boiler mass-balance reference. Its value lies in verifying that load, steam generation, feedwater and combustion-air delivery remain mutually consistent. Alerts should combine residual magnitude, persistence, operating state and corroboration across related variables; final fault attribution should use specific clusters.