# Cluster 3 - Draft System Balance

PA + SA + ID fan coordination: training data, validation and performance checking

| OBJECTIVE | Establish the normal coordination of PA, SA and ID fan systems with boiler load, steam flow and air delivery, and flag developing forced-draft/induced-draft imbalance before furnace-pressure excursion or fan overload. |
| --- | --- |

# Scope and Variables

Cluster 3 represents the boiler draft-system balance. The model will correlate fan speed/current and delivered airflow within user-defined load ranges. It should evaluate the combined response of the PA, SA and ID systems rather than treat individual tags independently. Draft system configuration of different boilers will be different.

Boiler Can have 1 x 100 % of all Fans or 2 x 100 % or 2 x 50% or it can have one Air Fan and 2 Gas Fans.

| Indicator | Calculation / relationship | Primary interpretation |
| --- | --- | --- |
| Demand / output | Load; Steam Flow-A; Steam Flow-B | Defines the expected draft-system duty. Steam Flow is primary key in this cluster as other parameters are dependent on Steam Flow. |
| Primary Air system | PA Fan A/B RPM and VFD Current; Total PA Flow, PA Head. | Relates PA fan effort to delivered primary air. |
| Secondary Air system | SA Fan A/B Speed and Current; SA Flow-A/B , SA Head. | Relates SA fan effort to delivered secondary air. |
| Induced Draft system | ID Fan A/B VFD Speed and Breaker Current, ID Head. | Represents flue-gas extraction effort. |
| Supporting air flow | TA Flow-A/B, where applicable | Completes the total incoming-air relationship. |
| Fuel Flow | Measured Fuel Flow (If Measured) | Gas Flow is dependent on Fuel Flow and Ash % in Fuel |
| Note | Tags and engineering units may vary by plant. | Project-specific adjustment and DCS verification are required. |

# Process Relationship to be Learned

LOAD / STEAM DEMAND  ->  PA + SA (+ TA) AIR INPUT  ->  COMBUSTION GAS  ->  ID FAN EXTRACTION

PA and SA fans push air into the boiler, while the ID fans remove the resulting flue gas. Their operating points must move together with boiler demand. Historical data should establish the accepted range for each load band and fan configuration.

## Load, Steam Flow and Draft-System Duty

Load and total steam flow are the primary demand references. User-defined load bands should follow boiler capacity, operating philosophy and historical data. For example, a 100 TPH boiler may use 90-100, 75-90, 60-75 and 40-60 TPH bands.

Total Main Steam Flow is validated as per Cluster 1.

If load and steam flow disagree, validate the demand reference using Cluster 1 before draft-system assessment.

Develop separate relationships for each valid PA, SA and ID fan combination where adequate data are available.

If two steam-flow measurements are in series, correlate both readings and apply a user-defined acceptable variation.

## Airflow and Fan-Effort Relationship

Total Secondary Air = SA Flow-A + SA Flow-B Total Tertiary Air = TA Flow-A + TA Flow-B Total Combustion Air = Total PA + Total SA + Total TA Total Gas Flow = Total Combustion Air + f(Fuel Flow)

Expected PA / SA Flow = f (Load or Steam Flow, Fan Speed, Fan Current) Expected ID Fan Response = f (Load or Steam Flow, Total Combustion Air,Fuel Flow) From Historical Data establish relationship of Load and Fan Current to check Incoming values.

# Training Relationships and Performance Indicators

| Relationship | Expected operating pattern | Condition to be flagged |  |
| --- | --- | --- | --- |
| Load/steam vs PA flow | Repeatable PA-flow range within each load band. | PA flow is outside the accepted demand-based range. |  |
| Load/steam vs SA flow | Repeatable SA-flow range within each load band. | SA flow is outside the accepted demand-based range. |  |
| Load PA/ SA Flow | PA/SA ratio at different Load Range | Ratio outside acceptable boundary. |  |
| Load PA/ ID/SA Current | Ratio from Historical Data, Create acceptable range for different Load Range | Raise alarm if any value beyond acceptable range. |  |
| PA/SA speed-current vs flow | Stable fan-effort-to-flow relationship. | More speed/current is required for comparable delivered flow. |  |
| Incoming air vs ID response | ID speed/current follows air input and boiler demand. | ID response is inconsistent with forced-draft duty. |  |
| Fan-A vs Fan-B | Comparable normalized response at similar duty. | Persistent A/B difference beyond the user-defined limit. |  |
| Fan Variable Residual = Actual Value - Predicted Value Normalized Residual (%) = (Actual - Predicted) / Predicted x 100 A/B Imbalance (%) = (A - B) / [(A + B) / 2] x 100 |  |  |

User-defined residual limits should be established for all Fan variables. Limits may vary by load band .. A value is accepted when its residual remains within the approved range; otherwise, the model flags the deviation for further validation.

## Combined PA-SA-ID Interpretation

PA or SA current/speed rises while delivered flow remains unchanged: fan/system effort has increased or a measurement has shifted.

ID speed/current rises without a corresponding change in load or incoming air: gas-path resistance, boiler air leakage (O2 % review); or signal quality requires review.

Forced-draft duty rises but the ID response does not follow verify operating state and correlate with furnace-pressure. (Will be part of different Cluster or RCA)

# Preparation for Training Data

Synchronize load, steam flow, fan speed/current and airflow tags to a common timestamp and sampling interval.

Classify every PA, SA and ID fan state: stopped, single fan, both fans, start/stop, changeover and manual/automatic operation.

Separate steady load, ramp-up, ramp-down, low load, start-up and shutdown data.

Exclude bad-quality, frozen, missing, impossible, maintenance-affected and known instrument-fault measurements. Long gaps should preferably not be interpolated.

Cover the full normal load range and valid fan combinations; do not allow one load band or configuration to dominate.

Retain valid variation caused by fuel, excess air, bed condition and control behaviour; remove only technically invalid data. We need establish acceptable operating range of a particular condition.

Important: Start-up, shutdown, fan changeover, trips and instrument-fault periods should not be mixed with healthy steady-state data. If sufficient data are available, create separate operating-state models for transient conditions.

# Data Validation Framework

| Validation layer | Minimum checks |
| --- | --- |
| Tag level | Missing data, frozen values, spikes, noise, impossible values, scaling and engineering-unit errors. |
| Equipment-state level | Fan run/stop, VFD availability, breaker/current-tag meaning, manual/auto mode, trip and changeover. |
| Relationship level | Demand-flow, fan effort-flow, incoming air-ID response and A/B normalized balance. |
| Operating-state level | Separate acceptable ranges for steady operation, ramps, low load and configuration change. |
| Cross-cluster level | Use furnace pressure, PA/SA distribution and flue-gas-path information to confirm the cause.(Can be covered in different Cluster or in a separate RCA) |

# Performance Checking

For each airflow, fan-speed and fan-current variable, the trained model should generate an expected value and accepted operating band for the applicable load range and equipment configuration. Performance is assessed using residual magnitude, persistence, data quality and correlation across PA, SA and ID systems.

| Residual = Actual Value - Predicted Value Accept value when ¦Residual¦ is within the user-defined limit Flag deviation when the limit is exceeded for the approved persistence time |  |  |
| --- | --- | --- |
| Observed pattern | Initial interpretation | Required validation |  |
| PA/SA speed or current high; flow normal | Higher fan/system effort or measurement error. | Check persistence, A/B residuals, pressure/distribution. |  |
| PA/SA flow low; fan effort normal/high | Delivered air is below the expected duty. | Check restriction, leakage, damper condition and flow measurement. |  |
| ID effort high; demand and inlet air normal | More gas-extraction effort is required than baseline. | Check furnace pressure, gas-path resistance, Excess Air and ID tag quality. |  |
| ID response low while PA/SA duty rises | Possible coordination/control deviation or transient. | Confirm operating state and furnace-pressure response. |  |
| A/B residual difference | One fan train differs from its own baseline or companion fan. | Confirm comparable duty and investigate deviation in details. |  |
| Multiple residuals persist | Higher-confidence draft-system imbalance. | Investigate using the relevant draft, pressure and maintenance clusters. |  |

## Recommended Dashboard Outputs

Actual, predicted and normal-band values for PA/SA airflow and PA, SA and ID fan speed/current.

Absolute and percentage residual, user-defined limit, persistence time and data-quality status.

Fan-A and Fan-B normalized residual trends.

## Model Acceptance and Review

Validate prediction error separately for each fan system, load band and equipment configuration.

Test the model on an independent period and verify that healthy operation remains within the accepted band.

Conclusion. Cluster 3 should establish the normal load-based coordination of PA, SA and ID fan systems with delivered airflow and fan effort. User-defined load bands and residual limits should validate each incoming value. Persistent combined deviations should be flagged early.