# Cluster 5 - PA Header & Total Flow

Training data relationships, validation logic and performance checking

| OBJECTIVE | Establish the normal relationship between boiler demand, total Primary Air flow and PA flow delivered through the HGG/header branches, and identify flow deficiency, imbalance or measurement deviation before combustion and fluidization are affected. |
| --- | --- |

# Scope and Variables

Cluster 5 is the combined PA header and total-flow cluster in the overall-cluster dependency matrix. HGG is specific to TKIL Boiler, so the above cluster is only applicable to TKIL installation having HGG. No of HGG is a plant specific input will depend on Boiler configuration.   Total PA Flow is the primary key and is benchmarked against main stream flow. The four PA-flow-to-HGG measurements provide supporting branch-flow information. HGG is only used during Start Up, so this model is used to validate data during Start Up condition.

| Indicator | Calculation / relationship | Primary interpretation |
| --- | --- | --- |
| Demand reference | Steam Flow-A; Steam Flow-B | Defines expected PA demand for each load range. Already defined in Cluster 2. |
| Primary key | Total PA Flow | Main PA output indicator. |
| HGG branch-A | PA Flow to HGG-A (1) and (2) | Validates A-branch delivery and redundant readings. |
| HGG branch-B | PA Flow to HGG-B (1) and (2) | Validates B-branch delivery and redundant readings. |
| Cross-cluster inputs | Load; PA fan status/speed/current; air-box pressure | Used for validation and fault isolation where available. |
| Note | Tags and units may vary by plant. | Project-specific adjustment and DCS verification are required. |

HGG Configuration is plant specific. Need Plant specific adjustment.

# Process Relationship to be Learned

LOAD / STEAM DEMAND ->  PA FAN OUTPUT ->  PA HEADER  ->  HGG / AIR-SIDE DELIVERY

As boiler production increases, total PA flow should increase within a plant-specific operating envelope. The relationship may not be perfectly linear because fuel quality, bed condition, fan combination, damper position and PA-system resistance affect the required flow. Historical data should therefore define a normal range for each user-defined load band and equipment configuration. During normal operation HGG should be out of service Normally operates at low load and Start- Up condition.

## Steam-Flow Reference and Load Bands

Validated Value from Cluster 1.

Load bands are user inputs based on capacity, operating philosophy and historical data; for a 100 TPH boiler, example bands may be 90-100, 75-90, 60-75 and 40-60 TPH.(Refer Cluster 1)

If the steam-flow reference is unreliable, validate it using Cluster 1 before scoring PA-header performance.

## Total PA Flow and Branch-Flow Relationship

Expected Total PA Flow = f (Steam Flow or Load, PA Fan Configuration) Expected HGG Branch Flow = f (Oil Flow in Branch, Coal Flow,Total PA Flow, Branch / Damper Configuration) Total HGG Flow/PA Flow Ratio=f(Steam Flow/ PA Flow)

The sum of available branch flows may be compared with Total PA Flow. The result should be treated as a calibrated historical balance, not an assumed exact equality.

# Training Relationships and Performance Indicators

| Relationship | Expected operating pattern | Condition to be flagged |  |
| --- | --- | --- | --- |
| Steam flow vs Total PA Flow | Repeatable PA-flow envelope in each load band. | Total PA Flow is outside the accepted demand-based range. |  |
| Total PA vs HGG branches | Stable branch share for a comparable configuration. | Branch contribution changes without a known operating change. |  |
| HGG A(1) vs A(2) | Track within an approved tolerance. | Persistent disagreement beyond the user-defined limit. |  |
| HGG B(1) vs B(2) | Track within an approved tolerance. | Persistent disagreement beyond the user-defined limit. |  |
| A-side vs B-side flow | Historically consistent distribution at comparable duty. | Developing side imbalance. |  |
| PA fan output vs Total PA | Normal flow for the applicable fan combination. | Fan effort and header flow become inconsistent. |  |
| PA Flow Residual = Actual Total PA Flow - Predicted Total PA Flow PA Flow Deviation (%) = PA Flow Residual / Predicted Total PA Flow x 100 Redundant Meter Deviation (%) = (Reading-1 - Reading-2) / [(Reading-1 + Reading-2) / 2] x 100 |  |  |

User-defined residual and meter-deviation limits should be established separately for each load band and fan/branch configuration. Incoming values are accepted when the residual remains within the approved range; otherwise, the model flags the deviation for validation.

As HGG configuration is not standard, Plant specific adjustments will be required.

## Branch Distribution Indicators

HGG-A Flow = validated combination of HGG-A (1) and HGG-A (2) HGG-B Flow = validated combination of HGG-B (1) and HGG-B (2) A/B Distribution Deviation (%) = (HGG-A Flow - HGG-B Flow) / [(HGG-A Flow + HGG-B Flow) / 2] x 100

The combination method may be an average for series measurements or a sum for parallel branches. The correct method must be confirmed from P&ID/DCS documentation. Equal A/B distribution should not be assumed; the accepted baseline should be developed from healthy historical operation.

# Preparation for Training Data

- Synchronize steam flow, Total PA Flow and all HGG branch-flow tags to a common timestamp and sampling interval.

- Classify PA fan configuration, branch/damper configuration, start/stop, changeover and manual/automatic operation.

- HGG is normally used during start up and low load so data availability may be limited. With limited data it may be a challenge to develop a reliable model.

- Exclude bad-quality, frozen, missing, impossible, maintenance-affected and known instrument-fault measurements. Long gaps should preferably not be interpolated.

- Retain valid changes caused by fuel, bed and control behavior; remove only technically invalid data.

Important: Model should mainly be for Startup and Low Load. If HGG is used at slightly higher load it should be investigated further.

# Data Validation Framework

| Validation layer | Minimum checks |
| --- | --- |
| Tag level | Missing data, frozen values, spikes, noise, impossible values, scaling and engineering-unit errors. |
| Relationship level | Steam flow-Total PA, Total PA-branch flow, A/B distribution. |

# Performance Checking

The deployed model should calculate expected Total PA Flow and expected branch-flow ranges for the applicable demand band and configuration. Performance is assessed using residual magnitude, persistence, data quality and cross-cluster consistency.

| Residual = Actual Value - Predicted Value Accept value when ¦Residual¦ is within the user-defined limit Flag deviation when the limit is exceeded for the approved persistence time |  |  |
| --- | --- | --- |
| Observed pattern | Initial interpretation | Required validation |  |
| Total PA low for steam demand | Insufficient header delivery or flow-measurement error. | Check PA fan performance, fan configuration and Total PA meter quality. |  |
| Total PA Normal; one HGG branch low | Downstream distribution, damper/duct restriction or branch-meter issue. | Compare redundant branch meters and air-box/distribution data. |  |
| A(1) and A(2), or B(1) and B(2), disagree | One flow measurement may be drifting. | Check calibration, impulse lines and measurement location. |  |
| Total PA high for demand | Excess PA delivery, control setting change or signal bias. | Check fan output, operating mode, fuel/bed condition and O2-related clusters. |  |
| A/B distribution shifts persistently | Developing side maldistribution or branch configuration change. | Confirm damper status and downstream pressure/temperature evidence. |  |
| Fan effort rises but Total PA does not | Higher PA-system resistance or fan/flow measurement issue. | Correlate with Clusters 2/3 and PA air-box distribution. |  |

## Recommended Dashboard Outputs

Actual, predicted and normal-band Total PA Flow by load band. (Already considered developed in Cluster 2)

HGG-A and HGG-B validated flow, and A/B distribution trend.

Absolute and percentage residual, user-defined limit.

## Model Acceptance and Review

Validate prediction errors separately by load band.

Test the model on an independent period and verify that healthy operation remains within the accepted limits.

Conclusion. Cluster 5 should establish the normal relationship between steam demand, Total PA Flow and HGG/header branch delivery. Persistent deviations should distinguish an overall PA-output problem from a branch-distribution or measurement problem .Cluster 5 mainly identifies deviation does not deep dive into RCA,