# Cluster 7 - ID Fan Performance

Training data relationships, validation logic and performance checking

| OBJECTIVE | Build a normal-behaviour model for ID Fan-A and ID Fan-B using load/steam demand, IDC feedback, motor current and fan RPM (Important Fan Parameters), and identify deterioration or control-response deviation before capacity or reliability is affected. |
| --- | --- |

# Scope and Variables

Cluster 7 groups each Induced Draft (ID) fan's control and electrical response against boiler production. The dependency matrix identifies the following training variables:

Fan Configuration are plant specific there may be 2 x 50%, 2 x 100 %, 1 x 100%

| Variable group | Fan-A tags | Fan-B tags | Role in model |
| --- | --- | --- | --- |
| Operating demand | Load; Steam Flow-A/B | Load; Steam Flow-A/B | Defines the expected ID duty. |
| Total Air Flow | F(Combination of Primary Air, Secondary Air, Tertiary Air) | F(Combination of Primary Air, Secondary Air, Tertiary Air) | Gas Flow is dependent on Total Air Flow |
| ID Fan Head | ID Fan A Head | ID Fan B Head | Fan Performance |
| ID Fan Flow | ID Fan A Flow | ID Fan B Flow | Fan Performance |
| Control position | ID Fan A IDC FB | ID Fan B IDC FB | Represents inlet-guide-vane feedback. Function of ID Duty. |
| Electrical response | ID Fan A VFD Current | ID Fan B VFD Current | Represents motor loading. Function of ID Duty. |
| Mechanical response | ID Fan A RPM | ID Fan B RPM | Represents delivered fan speed. Function of ID Duty. |

The source grouping states that a fan drawing more current or running at higher RPM than its load-based baseline may be degrading; possible areas for investigation include fouling, bearing condition and IGV linkage. The model should identify deviation to validate the incoming Value. RCA will be determined in separate RCA modules.

# Relationship Between Variables

## Boiler Demand and Required Fan Duty

Load and main steam flow(Validated value is generated in cluster 1) are reference variables for expected gas demand. As boiler demand rises, ID fan output generally has to increase. The model should learn the actual plant relationship by load band because fuel quality, bed condition, operating fan combination can modify the required response.

Load band is defined in cluster 1

Use both load and total steam flow to cross-check demand; a faulty load signal should not automatically be interpreted as fan deterioration. Use Cluster 1 to validate Steam Flow.

Separate single-fan, two-fan, changeover and transient operation if these states exist in the historical dataset.

## RPM, IGV Feedback and Motor Current

RPM and IDC feedback describe how the fan is being controlled; VFD current represents the electrical effort associated with the operating point. The trained model should predict the normal RPM, IGV feedback and current for each fan at the prevailing boiler demand and companion-fan condition.

Fan RPM=f(Fan Flow, Fan Head, Steam Flow, Total Air Flow) Fan IDC= f(Fan Flow, Fan Head, Steam Flow, Total Air Flow) Fan Current= f(Fan Flow, Fan Head, Steam Flow, Total Air Flow) Fan Residual = Actual Fan Variable - Predicted Fan Variable

# 3. Training Relationships and Diagnostic Features

The following relationships should be engineered as model inputs, calculated features or validation checks. Absolute limits should be finalized from approved design data and reviewed healthy operation; they should not be assumed from generic fan behavior.

| Relationship | Expected healthy pattern | Deviation requiring review |
| --- | --- | --- |
| Load / steam vs RPM | Repeatable, load-dependent fan-speed envelope. | Higher or lower RPM than predicted for sustained periods. |
| Load / steam vs current | Motor current follows required fan duty. | Current exceeds the load-based baseline or changes without demand change. |
| RPM vs current | Comparable electrical loading for comparable speed and operating state. | Current increases at similar RPM, indicating added resistance or mechanical/electrical loss. |
| IGV feedback vs RPM | Stable control combination for a given duty. | Unexpected IGV movement, saturation, oscillation or changed combination. |
| Fan-A vs Fan-B | Consistent normalized response when duties are comparable. | Persistent A/B residual difference under equivalent demand. |
| Steam flow vs load | Consistent demand reference. | Reference disagreement; validate process tags before fan assessment. |

When two similar fans operate in parallel, their operating parameters—such as speed, motor current, IGV position, discharge pressure and flow—should normally remain within a historically established relative-difference range. However, exact equality should not be expected because of normal differences in system resistance, damper position, instrument accuracy and load sharing.

A small and stable difference indicates normal unequal load sharing. A sudden increase or a continuously rising difference may indicate a change in operating condition between the two fans.

A deviation should be flagged when the relative difference exceeds a user-defined limit for a specified persistence time. Final diagnosis should consider the combined behaviour of current, speed, IDC feedback, pressure and flow rather than relying on one parameter alone.

## Recommended Calculated Indicators

Current Deviation (%) = (Actual Current - Predicted Current) / Predicted Current x 100

RPM Deviation (%) = (Actual RPM - Predicted RPM) / Predicted RPM x 100

A/B Current Imbalance (%) = (Current-A - Current-B) / [(Current-A + Current-B) / 2] x 100

A/B RPM Imbalance (%) = (RPM-A - RPM-B) / [(RPM-A + RPM-B) / 2] x 100

A/B imbalance is meaningful only when both fans have comparable duty and are in a comparable control state. If load sharing is intentionally unequal, comparison should use model residuals or normalized duty rather than raw current or RPM.

# Training Data Preparation

- Synchronize load, steam flows, IGV feedback, VFD current and RPM to one timestamp and common sample interval.

- Retain fan running/stopped status if available; remove stopped-fan values from the running-performance model. Fan running conditions can be determined from Fan Speed.

- Classify fan operation: Fan-A only, Fan-B only, both fans, start/stop, changeover and abnormal/manual operation.

- Separate steady-state and transient data. Define steady-state using reviewed load and flow stability criteria.

- Remove bad-quality, frozen, missing, impossible, maintenance-affected and known instrument-fault periods.

- Check time lag among demand, RPM, IGV feedback and current before applying any time shift.

- Balance training data across load bands and fan configurations; prevent one frequently used condition from dominating.

Model boundary: Cluster 2 evaluates fan control/electrical response relative to demand. PA pressure and downstream air-distribution variables should be used from the relevant draft and distribution clusters for diagnosis confirmation.

# Data Validation Framework

| Validation layer | Checks before training or scoring |
| --- | --- |
| Tag quality | Missing values, bad quality, frozen readings, spikes, noise, scaling/unit error and impossible values. |
| Equipment state | Fan run/stop, VFD availability, manual/auto mode, changeover, trip and maintenance state where available. |
| Relationship | Demand-RPM, demand-current, RPM-current, IGV-RPM and A/B normalized response. |
| Operating state | Separate steady load, ramps, low load, start-up, shutdown and fan-configuration change. |
| Cross-cluster | Confirm abnormal fan residuals using PA pressure/flow, draft and downstream distribution evidence. |

## Validation Rules for Model Inputs

Do not replace long data gaps with interpolation; mark the interval unavailable for model assessment.

Treat sudden step changes in only one measurement as a probable data-quality event until corroborated.

# Performance Checking

The deployed model should calculate expected IDC feedback, RPM and current for each fan and compare them with actual values. Alarm logic should combine residual magnitude, persistence, data quality and supporting variables rather than trigger on a single instantaneous excursion. Expected value will be determined by Machine Learning method of historical data.

| Observed residual pattern | Initial interpretation | Required confirmation |
| --- | --- | --- |
| Current high; RPM and demand normal | Additional electrical/mechanical loading or current measurement issue. | Check persistence, A/B comparison, maintenance data and related pressures/flows. |
| RPM high for normal demand | More speed is required than the learned baseline. | Check system resistance(ID Fan draft), air delivery and fan control state. |
| IGV feedback abnormal for RPM/demand | Control-position or feedback relationships have changed. | Verify command vs feedback, linkage/actuator condition and operating mode. |
| A/B residual divergence | One fan behaves differently from its own baseline or companion fan. | Confirm equal duty and compare downstream A/B air conditions. |
| All fan variables shift with load reference mismatch | Demand input may be unreliable, or operation is transient or Fan deterioration issue requiring investigation. | Validate load and steam-flow relationship before fan diagnosis. |
| Multiple fan residuals persist with process deviation | Higher-confidence fan/system performance issue. | Escalate for cross-cluster and field verification. |

## 6.1 Dashboard and Model Acceptance

Display actual, predicted and normal-band values for current, RPM and IDC feedback for each fan.

Show residual percentage, duration, data-quality status, fan configuration and operating-state label.

Trend Fan-A and Fan-B normalized residuals on the same view for side-by-side comparison.

Conclusion. Cluster 7 provides a load-referenced normal-behaviour model for ID Fan-A and ID Fan-B. The most useful performance signal is a sustained change in the relationship among demand, RPM, IDC feedback and motor current. The cluster should flag deterioration or control inconsistency early, while root-cause assignment must be confirmed using data quality, operating state, ID pressure/flow, air distribution and maintenance evidence in a separate RCA model.