Cluster 8 – SA Air Distribution

TECHNICAL NOTE  |  BOILER PERFORMANCE ANALYTICS

Training relationships, validation logic and performance checking

| OBJECTIVE | Build a normal-behaviour model for secondary-air pressure, flow and temperature delivery from the APH outlet to the furnace, referenced to steam demand, so that SA-side restriction, leakage, maldistribution or heat-pickup deterioration is detected early. |
| --- | --- |

# Scope and Variables

Cluster 6 evaluates whether secondary air is delivered to the furnace in the quantity, pressure and temperature expected for the prevailing steam demand. It complements the fan and draft clusters by focusing on the downstream SA distribution path rather than on fan electrical health.

| Variable group | Tags | Role in model |
| --- | --- | --- |
| Operating demand | Steam Flow-A; Steam Flow-B | Defines the expected combustion duty and load band. |
| Upstream pressure | SA PR TO APH(A); SA PR TO APH(B) | Represents pressure delivered toward/through the APH on each side. |
| Furnace delivery pressure | sa Pressure At Furnace Inlet; SA PR TO FURNACE | Represents usable SA pressure reaching the furnace. |
| Temperature delivery | SA TEMP TO FURNACE; SA TEMP TO FURNACE [2] | Represents SA heat pickup and provides redundant/parallel temperature evidence. |
| Air-box temperature | AIR TEMP AT AIR BOX A; AIR TEMP AT AIR BOX B | Provides side-level thermal distribution evidence. Ideally SA Temperature to Furnace and Air box Temperature are same. |
| Flow delivery | SA FLOW-A; SA FLOW-B | Measures the secondary-air quantity delivered by each side. |

Tag confirmation: Confirm pressure tapping locations, temperature sensor locations, units, and whether the two furnace-temperature tags are redundant, serial or side-specific before model training.

# Process Relationships to Be Learned

## Steam Demand and Required SA Flow

Total main steam flow is the production reference. Under healthy steady operation, total SA flow should follow a repeatable, load-dependent envelope; the relationship can shift with fuel quality, excess-air strategy, bed condition and PA/SA/TA distribution.

Total Main Steam Flow = Validated Main Steam Flow

Total SA Flow = SA Flow-A + SA Flow-B

Expected Total SA Flow = f(Total Main Steam Flow, operating state)

## Pressure Delivery and Distribution

The pressure chain should remain internally consistent from the APH-side measurements to the furnace inlet. A growing pressure drop at comparable flow may indicate APH/duct restriction, damper movement or fouling; reduced pressure without a flow increase may indicate leakage or measurement drift.

SA Path Pressure Drop = Representative SA Pressure to APH − SA Pressure to Furnace (Function of SA Flow)

SA Flow Side Imbalance (%) = (SA Flow-A − SA Flow-B) / [(SA Flow-A + SA Flow-B)/2] × 100

## Temperature Delivery

SA temperature reflects air-preheater heat pickup and downstream heat loss. The model should learn temperature versus steam demand and operating state rather than apply one fixed target. Side or redundant-sensor divergence should be tracked separately from overall temperature deterioration.

A/B Air-Box Temperature Difference = Air Box Temp-A − Air Box Temp-B

Furnace SA Temperature Residual = Actual − Predicted

# Training Relationships and Diagnostic Features

| Relationship | Healthy pattern | Deviation requiring review |
| --- | --- | --- |
| Steam flow vs total SA flow | Repeatable nonlinear envelope by load band. | Sustained high/low SA flow for the same steam demand. |
| SA flow A vs B | Stable normalized split for comparable side duty. | Persistent imbalance or progressive drift. |
| Flow vs pressure | Repeatable pressure requirement for delivered flow.SA Fan Dis | Higher pressure drop at similar flow or reduced flow at similar upstream pressure. |
| APH-side vs furnace pressure | Stable path loss by flow/load band. | Increasing path pressure loss or unexpected pressure collapse. |
| Steam flow vs SA temperature | Stable heat-pickup envelope by operating state. | Sustained low/high delivery temperature. |
| Temperature A vs B / sensors | Stable side or sensor difference. | Divergence, frozen value, common-mode shift or implausible step. |
| Cross-cluster consistency | SA delivery agrees with fan/draft and combustion response. | Distribution residual without corresponding fan-demand change. |

## Recommended Calculated Indicators

SA Flow Deviation (%) = (Actual Total SA Flow − Predicted Total SA Flow) / Predicted Total SA Flow × 100

SA Pressure-Loss Deviation = Actual Path Pressure Drop − Predicted Path Pressure Drop

SA Temperature Deviation (%) = (Actual Temperature − Predicted Temperature) / Predicted Temperature × 100

Residual of all measurements must be within acceptable band. If residual is within acceptable limit incoming value is validated. Reason of deviation can be analyzed in a separate RCA module.

# Training Data Preparation

Synchronize steam flows, SA pressures, flows and temperatures to a common timestamp and sample interval.

Classify steady load, ramp-up/down, low load, start-up, shutdown, fan/damper changeover and manual-control periods.

Remove bad-quality, frozen, missing, impossible and maintenance-affected values; do not interpolate long gaps.

Balance healthy training data across load bands and normal A/B configurations.

Retain known degraded or fouled periods for independent detection testing, not healthy training.

Model boundary: Cluster 8 isolates SA distribution performance.

# Data Validation Framework

| Validation layer | Checks before training or scoring |
| --- | --- |
| Tag quality | Missing/frozen data, spikes, noise, impossible values, unit/scaling errors and sensor disagreement. |
| Operating state | Stable load versus ramps, start-up/shutdown, fan starts/stops, damper changes and manual operation. |
| Relationship | Steam-flow/SA-flow, flow/pressure, upstream/furnace pressure and temperature-load consistency. |
| Side balance | A/B flow, APH pressure and air-box temperature normalized for intended side duty. |
| Cross-cluster | Confirm with SA fan condition, furnace draft, O₂, fuel and bed-temperature behaviour. |

# Performance Checking and Diagnostics

| Observed residual pattern | Initial interpretation | Required confirmation |
| --- | --- | --- |
| Total SA flow low; demand normal | Insufficient SA delivery or flow measurement issue. | Check pressure chain, fan/damper state, O₂ and combustion response. |
| Path pressure loss high at similar flow | Developing APH/duct restriction or damper throttling. | Verify damper position, cleanliness and pressure-tap health. |
| Pressure low with unexplained flow loss | Leakage, upstream delivery weakness or pressure measurement drift. | Compare fan/draft cluster and inspect duct/expansion joints. |
| A/B flow or temperature divergence | Side maldistribution, side restriction or sensor drift. | Confirm intended split and compare side pressures. |
| SA temperature low at normal demand | Reduced APH heat pickup, bypass/leakage or sensor issue. | Compare flue-gas temperatures and APH condition. |
| Multiple persistent residuals | Higher-confidence SA distribution degradation. | Escalate for cross-cluster and field verification. |

## Dashboard and Model Acceptance

Display actual, predicted and normal-band values for total SA flow, A/B flows, furnace pressure and SA temperatures.

Show path pressure drop, A/B imbalance, residual magnitude, persistence, data-quality status and operating-state label.

Evaluate model errors separately by load band, steady/transient state and side/configuration.

Conclusion. Cluster 8 provides the downstream secondary-air distribution health model. The strongest warning is a sustained change in the learned relationship among steam demand, SA flow, pressure delivery and temperature. Root cause should be assigned only after checking operating state, instrumentation and corroborating fan, draft and combustion evidence.