Cluster 9 – Flue Gas Path / ESP / Economiser-1

TECHNICAL NOTE |  BOILER PERFORMANCE ANALYTICS

Training relationships, validation logic and performance checking

| OBJECTIVE | Build a normal-behaviour model for flue-gas temperature and pressure from the ESP inlet through Economiser-1 and toward the stack, referenced to steam demand, to identify gas-side fouling, abnormal draft loss, ESP restriction and deterioration in Economiser-1 heat pickup. |
| --- | --- |

# 1. Scope and Variables

Cluster 9 is the common-header gas-path cluster. It tracks how flue-gas pressure and temperature evolve through the ESP and Economiser-1 region. Oxygen is intentionally excluded from this cluster and should be brought in from the combustion cluster for diagnostic confirmation.

| Variable group | Tags | Role in model |
| --- | --- | --- |
| Operating demand | Steam Flow-A; Steam Flow-B | Defines expected gas generation and heat-release duty. Can be correlated with Cluster 7. |
| ESP temperature | FG TEMP BEFORE ESP; FG TEMP AFTER ESP | Measures thermal condition across the ESP section. |
| ESP pressure | PG PR BEFORE ESP; FG PR AFTER ESP | Measures gas-path pressure before and after ESP. |
| Economiser-1 inlet | FG I/L PR TO ECO-1; FG TEMP ECO-1 I/L; | Defines inlet gas condition and provides pressure cross-checking. |
| Economiser-1 outlet | CO O/L TO ECO-1; FG TEMP AT ECO-1 O/L, FG PR ECO-1 O/L, O2 ECO – 1 O/L | Defines outlet condition; tag “CO O/L TO ECO-1” requires site confirmation. |
| Airheater outlet | CO O/L TO ECO-1; FG TEMP AT ECO-1 O/L, FG PR ECO-1 O/L |  |
| Stack approach (Additional Information) | FG TEMP BEFORE STACK.IT IS AN ADDITIONAL MEASUREMENT CAN BE CORELATED WITH ESP OUTLET TEMPERATURE. | Provides downstream exhaust-temperature evidence. |

Tag confirmation: The matrix contains “PG PR BEFORE ESP” and “CO O/L TO ECO-1”. Confirm whether these are typographical tag names, their measured quantities, locations and engineering units before use.

# 2. Process Relationships to Be Learned

## 2.1 Steam Demand and Flue-Gas Condition

Steam flow is the production reference. As firing increases, flue-gas quantity and temperature generally change, but the relationship is affected by fuel quality, excess air, sootblowing, heat-transfer cleanliness and equipment configuration. The model should therefore learn load-dependent envelopes from reviewed healthy data.

Total Main Steam Flow = Validated Steam Flow from Cluster 1

Expected FG Temperature/Pressure = f(Total Main Steam Flow, operating state)

## ESP Pressure Loss

Pressure loss across the ESP should be evaluated at comparable steam demand and gas-flow conditions. A sustained increase may indicate increased gas flow, ash loading, hopper/field obstruction or gas-path restriction; a sudden isolated change may instead be a pressure-transmitter problem.

ESP Differential Pressure = Pressure Before ESP − Pressure After ESP

ESP DP Residual = Actual ESP DP − Predicted ESP DP

## Economiser-1 Heat Pickup

The flue-gas temperature reduction through Economiser-1 is an indicator for gas-side heat pickup when compared at stable demand. A reduced drop can indicate fouling or changed water-side conditions; an increased drop can reflect operating-state change, excess-air variation or sensor bias. Water-side confirmation should be obtained from the feedwater/economiser cluster.

Eco-1 Gas Temperature Drop = FG Temperature at Eco-1 Inlet − FG Temperature at Eco-1 Outlet

Eco-1 Temperature-Drop Residual = Actual ΔT − Predicted ΔT

## Overall Gas-Path Trend to Stack

The temperature after ESP. Its residual should be interpreted together with upstream temperatures; one inconsistent tag is more likely an instrumentation issue, while a coherent multi-point shift indicates a process or heat-transfer change.

# Training Relationships and Diagnostic Features

| Relationship | Healthy pattern | Deviation requiring review |
| --- | --- | --- |
| Steam flow vs FG temperatures | Repeatable temperature enveloped by load band. | Persistent common or local temperature shift. |
| Before vs after ESP pressure | Stable load-dependent ESP pressure loss. | Rising DP, sudden collapse or inconsistent pressure ordering. |
| Before vs after ESP temperature | Small, stable section-specific change. | Unexpected temperature divergence or isolated sensor drift. |
| Eco-1 inlet vs outlet temperature | Repeatable gas-side temperature drop. | Reduced/increased ΔT at similar demand. |
| Eco-1 pressure profile | Consistent pressure progression through gas path. | Additional pressure loss or implausible pressure reversal. |
| Eco-1 outlet vs Air heater outlet | Stable downstream thermal progression. | Unexpected heat loss/gain . |
| Cross-cluster consistency | Draft, combustion and water-side variables corroborate. | Gas-path residual without supporting process evidence. |

## Recommended Calculated Indicators

ESP DP Deviation (%) = (Actual ESP DP − Predicted ESP DP) / ¦Predicted ESP DP¦ × 100

Eco-1 Heat-Pickup Index = T(Eco-1 inlet) − T(Eco-1 outlet)

Airheater Heat- Pickup Index= T(Eco-1 Outlet) − T(APH outlet)

Pressure-Profile Consistency = ordered comparison of all validated pressure taps

Temperature-Profile Consistency = ordered comparison of all validated Temperature taps

# Training Data Preparation

Synchronize all flue-gas pressures, temperatures and steam flows to one timestamp and sample interval.

Classify steady load, ramps, start-up/shutdown, ESP field/hopper events, sootblowing and equipment-change periods.

Remove bad-quality, frozen, missing, impossible, calibration-affected and maintenance-affected values.

Keep known fouling, ESP restriction and post-cleaning periods for independent detection and sensitivity testing.

Model boundary: Cluster 9 detects downstream gas-path and heat-transfer deviations. ESP electrical field performance is not represented by the listed tags, and Economiser-1 root-cause assessment requires water-side evidence from Cluster 8 and combustion/draft evidence from other clusters.

# Data Validation Framework

| Validation layer | Checks before training or scoring |
| --- | --- |
| Tag quality | Missing/frozen values, spikes, noise, range/unit errors, sign convention and redundant-tap disagreement. |
| Operating state | Steady load versus ramp, sootblowing, ESP/hopper events, start-up, shutdown and maintenance. |
| Pressure profile | Physically consistent ordering and load-dependent DP across ESP/Eco-1 sections. |
| Temperature profile | Consistent upstream/downstream progression and plausible section temperature drops. |
| Cross-cluster | Confirm with ID-fan/draft, fuel/O₂/bed temperature and feedwater/Economiser-2 evidence. |

# 6. Performance Checking and Diagnostics

| Observed residual pattern | Initial interpretation | Required confirmation |
| --- | --- | --- |
| ESP DP high; demand stable | ESP/gas-path restriction or pressure measurement bias. | Check persistence, hopper/ash condition, ESP operation and pressure taps. |
| Eco-1 ΔT reduced; inlet condition normal | Reduced heat pickup or changed water-side condition. | Check feedwater conditions, sootblowing and surface cleanliness. |
| Eco-1 ΔT increased unexpectedly | Operating condition change or sensor bias. | Validate excess air, demand, water side and temperature sensors. |
| Stack temperature high with upstream shift | Reduced downstream heat recovery or excess gas/air. | Cross-check combustion, APH and water-side clusters. |
| Single temperature/pressure tag steps | Likely instrument/data-quality event. | Look for corroboration before equipment diagnosis. |
| Multiple coherent pressure and temperature residuals | Higher-confidence gas-path degradation. | Escalate for cross-cluster and field verification. |

## 6.1 Dashboard and Model Acceptance

Display actual, predicted and normal-band values for each temperature and pressure tag.

Show ESP DP, Eco-1 temperature drop, APH Outlet-temperature residual, persistence and data-quality status..

Evaluate errors by load band, fuel regime and steady/transient state; avoid relying on overall average accuracy.

Conclusion. Cluster9 provides the common flue-gas-path health model from the ESP region through Economiser-1. The most reliable alert is a persistent, physically consistent change in pressure loss or temperature profile at comparable steam demand. Final diagnosis must combine tag quality, operating state, draft, combustion and water-side evidence will be carried in a separate RCA model.