# Cluster 2 — PA Fan Performance — Validation Report

Source: backend/clusters/docs/Cluster_2_PA_Fan_Performance_Technical_Note Final.docx Data: data/raw/boiler9_cleaned_2024.csv, 91,767 rows, 2024-01-18 00:00:00 to 2024-12-31 23:55:00

Standalone offline pipeline, same phased methodology as Cluster 1 (Load-Flow Mass Balance) — read the doc, verify real tag availability (Step 0), build config -> baseline -> validator (Steps 1-3), produce this report (Step 4). Not wired into any live module or dashboard — by design, same scope limitation as Cluster 1.

Read this before the numbers below: because PA Fan Head is unavailable and Load doesn't explain Fan Flow in this plant's real data (section 1.3), this model answers "is each fan's RPM/Current/IGV internally consistent with its own measured Flow?" — not "is the fan correctly responding to boiler demand?", which is what Table 3's original demand-referenced framing (f(Fan Flow, Fan Head, Steam Flow)) implied. That's still a valid and useful diagnostic — a fan whose speed/current/IGV don't match its own Flow is a real signal worth investigating — but it is a different question than the doc originally posed, and a residual flagged here does not by itself mean the fan is failing to keep up with demand.

## 1. Methodology

### 1.1 Head decision (Step 0)

No "PA Fan A Head" / "PA Fan B Head" tag exists anywhere in the raw historian. Exactly ONE PA-side pressure tag exists at all (PA PR TO HGG), and it is a byte-identical duplicate of PA PR TO APH (A) (verified via pandas.Series.equals() across all 91,767 rows) — the same physical tap logged twice under two names, not two real readings. No (B) counterpart exists (unlike SA, which genuinely has both SA PR TO APH(A) and SA PR TO APH(B)).

Decision (user, 2026-08-11): Head is dropped from all three relationship formulas (doc Table 3: Fan RPM/IGV/Current = f(Fan Flow, Fan Head, Steam Flow), reduced here to f(Fan Flow)). This is a config-driven decision — clusters/cluster2_config.yaml's relationships.*.stratify_by lists currently read [FLOW] only; adding a real per-fan Head tag later (status: available) and appending HEAD to a relationship's stratify_by list is intended to be sufficient, with no baseline/validator code change, since cluster2_baseline.py's binning is written generically over however many stratify_by columns are configured (see 1.3).

A candidate Head substitute was found and is extracted for reference only, NOT used in any relationship: PA PR AT AIR BOX A/B/C — three real, clean, independently-varying pressure tags downstream at the windbox. Not the same physical point as fan discharge head, and the A/B/C-to-fan-A/B correspondence is unconfirmed (a third "C" zone has no obvious fan mapping at all) — flagged for Punarbasu, not silently adopted.

### 1.2 Training / test split and filters

Same monthly-stratified 20/80 chronological split as Cluster 1 (shared/chronological_split.py) — trains only on the first 20% of each calendar month's own span, scores the remaining ~80% (genuinely unseen).

Total rows: 91,767

Training window: 18,340 rows

STEADY-only (of training window): 18,279 rows ({'STEADY': 18279, 'LOW_LOAD': 61})

Fan-running-only (of STEADY training rows, per side — see 1.4): A: 18,279, B: 18,279

Test window (scored by the validator): 73,427 rows

Split diagnostics: 11 calendar months with data, 10 sampling gap(s) in the full dataset (see shared/chronological_split.py).

### 1.3 Flow-binned baseline, not Load-binned — checked empirically, range-restriction ruled out

Module 1/Cluster 1 both bin by LOAD using fixed edges [0,80,90,100,110,120] (% MCR). Cluster 2 does NOT reuse those edges — checked first, not assumed:

corr(Load, Fan-A Flow) = 0.139, corr(Load, Fan-B Flow) = 0.106 — essentially no linear relationship in this real dataset.

corr(Fan-A Flow, Fan-B Flow) = 0.994 — the two fans' own flows track each other almost perfectly.

Range-restriction check. A weak correlation between two variables that both occupy a narrow range can be a statistical artifact, not a real absence of relationship — Load itself is compressed to ~87-111% MCR nearly all year (CV 3.88%), and Flow's own range is narrow too (CV 2.51-2.52%), so this was checked directly rather than assumed away:

If Load genuinely drove Flow, conditioning on a narrow Load slice should shrink Flow's spread well below its unconditional (whole-dataset) spread — that's what "Load explains Flow's variance" means. Computed directly: binning Load into 1-percentage-point-wide bins (e.g. exactly 100-101% MCR, n=10,735) and comparing each bin's Flow std against Flow's unconditional std.

Result: the average within-Load-bin Flow std is 101.1% of Flow's unconditional std (Fan A) and 100.2% (Fan B) — i.e. knowing Load to within one percentage point explains approximately ZERO of Flow's variance, not just "not much." Within a single narrow load bin (n>10,000 rows, load pinned at 100-101%), Fan A Flow still ranges 33.6-42.4 tph — nearly its entire full-dataset range (33.5-43.9 tph). In r² terms (variance explained under a linear model), Load explains ~1.95% of Fan A Flow's variance and ~1.13% of Fan B's.

This rules out range restriction as the explanation for the weak correlation — if it were a range-restriction artifact, narrowing the Load window further should have revealed Flow tightening up correspondingly, and it does not. Flow is genuinely driven by something independent of demand in this plant's real 2024 operation (most likely damper/IGV position or fan-combination/control choices not captured by Load alone) — a materially different physical story from the doc's own framing ("As boiler demand rises, PA fan output generally has to increase"), not merely a data-availability caveat.

Given the doc's own Table 3 formula treats Fan Flow (not Load) as the primary input, and Load demonstrably doesn't explain Flow variance in this plant's real 2024 data (confirmed above, not a range artifact), each relationship's baseline is binned by the fan's OWN Flow instead. Flow has no natural "% of something" scale the way Load does, so bin edges are QUANTILE-based (5 bins by default, n_bins in cluster2_config.yaml), computed from the STEADY+running training data itself, with the outer edges widened to +/-inf so any scoring-time value always falls in some bin.

### 1.4 Fan-running derivation and fan-configuration mix — checked empirically

No dedicated fan run/stop/trip tag exists for either fan (confirmed, Step 0). Derived from RPM per the doc's own suggestion ("Fan running condition can be determined from Fan Speed") — both fans' RPM sit at 1085+ for 99.9%+ of the year, with a clean, wide gap down to two real exceptions — fan_running.rpm_threshold: 500 (RPM) in cluster2_config.yaml sits cleanly in that gap.

Fan-configuration mix: this plant runs BOTH PA fans essentially continuously through 2024 — 99.93%+ of rows have both fans above the running threshold. Two exceptions exist, confirmed distinct in nature (checked at raw-tag resolution, not assumed identical just because both trip the same guard):

1. 2024-03-21, ~08:00-13:30 (widest window the guard trips across; the sharpest near-zero dip in current specifically is a narrower ~10:15-13:20 sub-window) — Fan A's RPM/current/IGV all decay together while Fan B's RPM/current visibly rise to compensate. A physically coherent single-fan-stop signature — a genuine operational event (see section 4's "Multiple fan residuals" worked example, drawn from this event).

2. 2024-02-11 13:25-13:30 (2 rows) — BOTH fans' RPM/current drop together, immediately followed by a 25-minute historian sampling gap (13:35-13:55), then both recover together at 14:00. This timestamp is already documented in shared/data_quality.py's KNOWN_BAD_TIMESTAMPS as a Steam Flow-B glitch coinciding with a broader logging hiccup — this reads as the same brief data-quality/logging dropout affecting both fans at once, not a new finding about fan behavior or a second operational configuration change.

No per-configuration baselines are built (Fan-A-only / Fan-B-only / changeover) — there is no meaningful training population for any configuration other than "both running," checked empirically rather than assumed, per the brief's explicit instruction.

### 1.5 A/B imbalance baseline — a real bug found and fixed during Step 3

Applying the doc's literal formula, A/B Current Imbalance (%) = (Current_A - Current_B) / avg * 100, and flagging anything beyond a fixed threshold around 0%, was tried first and produces a false alarm on essentially every row: Fan A and Fan B draw structurally different current at comparable duty/RPM in this plant (Fan A mean ~328 A, Fan B mean ~532 A — a stable ~-47.2% offset, IQR -47.5% to -46.8%, std only 0.62 percentage points during STEADY+comparable-duty operation). RPM imbalance, by contrast, genuinely IS centered near zero (-0.41% mean).

This matches the doc's own Table 4 framing exactly: "A small and stable difference indicates normal unequal load sharing... A sudden increase or a continuously rising difference may indicate a change" — the doc anticipates a non-zero, stable baseline, not that 0% is automatically "normal." Fixed by giving both imbalance metrics their own LEARNED STEADY-state band (global, not Flow-binned — the doc frames this as "stable," not load-dependent), and scoring actual imbalance against that learned band instead of a fixed threshold at zero. The underlying cause of the ~47% structural current offset (different motor/fan capacity rating, or different current- transformer scaling between the two fans) is an open item for Punarbasu (see section 5) — this report does not resolve it, only avoids mischaracterizing it as a fault.

## 2. Parameters, thresholds and tolerances (all user-configurable)

Per the doc's own instruction — "Absolute limits should be finalized from approved design data and reviewed healthy operation; they should not be assumed from generic fan behavior" — every number below is a reasonable configurable default pending plant validation, not a doc-given value (only the formulas themselves, doc Table 3/5, are used verbatim).

| Setting | Value | Source |
| --- | --- | --- |
| fan_rpm.band_width_std | 2.0 | configurable default |
| fan_rpm.stratify_by | ['FLOW'] | Step 0 decision, see 1.1 |
| fan_rpm.n_bins | 5 | configurable default |
| fan_igv.band_width_std | 2.0 | configurable default |
| fan_igv.stratify_by | ['FLOW'] | Step 0 decision, see 1.1 |
| fan_igv.n_bins | 5 | configurable default |
| fan_current.band_width_std | 2.0 | configurable default |
| fan_current.stratify_by | ['FLOW'] | Step 0 decision, see 1.1 |
| fan_current.n_bins | 5 | configurable default |
| ab_imbalance_guard.comparable_duty_tolerance_pct | 15.0 | configurable default |
| ab_imbalance_guard.band_width_std | 2.0 | configurable default |
| fan_running.rpm_threshold | 500.0 RPM | empirically chosen, see 1.4 |
| baseline.min_samples | 20 | configurable default, same as Cluster 1 |
| persistence.minutes | 15 | configurable default — not implemented this phase, see section 6 |

## 3. Summary status by relationship

Scored across the full test window (73,427 rows, unseen by training).

### fan_a_rpm

| status | rows | % |
| --- | --- | --- |
| consistent | 68,711 | 93.58% |
| outlier | 4,648 | 6.33% |
| unknown | 68 | 0.09% |

### fan_a_current

| status | rows | % |
| --- | --- | --- |
| consistent | 69,282 | 94.35% |
| outlier | 4,077 | 5.55% |
| unknown | 68 | 0.09% |

### fan_a_igv

| status | rows | % |
| --- | --- | --- |
| consistent | 73,348 | 99.89% |
| outlier | 10 | 0.01% |
| unknown | 69 | 0.09% |

### fan_b_rpm

| status | rows | % |
| --- | --- | --- |
| consistent | 69,463 | 94.60% |
| outlier | 3,963 | 5.40% |
| unknown | 1 | 0.00% |

### fan_b_current

| status | rows | % |
| --- | --- | --- |
| consistent | 69,976 | 95.30% |
| outlier | 3,450 | 4.70% |
| unknown | 1 | 0.00% |

### fan_b_igv

| status | rows | % |
| --- | --- | --- |
| consistent | 26,094 | 35.54% |
| outlier | 42,737 | 58.20% |
| unknown | 4,596 | 6.26% |

### ab_current_imbalance

| status | rows | % |
| --- | --- | --- |
| consistent | 71,149 | 96.90% |
| outlier | 2,210 | 3.01% |
| ambiguous | 66 | 0.09% |
| unknown | 2 | 0.00% |

### ab_rpm_imbalance

| status | rows | % |
| --- | --- | --- |
| consistent | 73,343 | 99.89% |
| outlier | 16 | 0.02% |
| ambiguous | 66 | 0.09% |
| unknown | 2 | 0.00% |

### Diagnostic pattern occurrence (doc section 6 table)

| pattern | rows |
| --- | --- |
| Current high; RPM and demand normal | 2,456 |
| RPM high for normal demand | 2,861 |
| IGV feedback abnormal for RPM/demand | 39,424 |
| A/B residual divergence | 2,213 |
| All fan variables shift with load reference mismatch | 500 |
| Multiple fan residuals persist with process deviation | 8 |
| (no flagged pattern — healthy) | 25,965 |

## 4. Worked examples — one real case per residual pattern

Per the brief: at least one real outlier case per row of the doc's residual-interpretation table (section 6), pulled from this report's own test-window scoring — none forced; every pattern below genuinely occurs in the 2024 data (unlike Cluster 1's SHUTDOWN case, which never occurred at all — Cluster 2 has no such absent pattern to report).

### Current high; RPM and demand normal

2024-12-25 10:10:00 — Load 100.7% MCR

> Additional electrical/mechanical loading or current measurement issue. > > Required confirmation (doc, unmodified): Check persistence, A/B comparison, maintenance data and related pressures/flows.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A RPM | 1105.96 | 1146.54 | -3.54% |
| Fan A Current | 303.45 | 317.18 | -4.33% |
| Fan A IGV FB | 101.00 | 100.44 | +0.56% |
| Fan B RPM | 1108.64 | 1152.05 | -3.77% |
| Fan B Current | 491.28 | 513.50 | -4.33% |
| Fan B IGV FB | 101.00 | 100.53 | +0.47% |
| A/B Current Imbalance | -47.27% | baseline -47.21% ± 0.62% | — |

### RPM high for normal demand

2024-04-26 14:00:00 — Load 101.6% MCR

> More speed is required than the learned baseline. > > Required confirmation (doc, unmodified): Check PA-system resistance, air delivery and fan control state.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A RPM | 1195.05 | 1167.63 | +2.35% |
| Fan A Current | 330.47 | 326.96 | +1.07% |
| Fan A IGV FB | 101.00 | 100.47 | +0.52% |
| Fan B RPM | 1201.18 | 1171.24 | +2.56% |
| Fan B Current | 533.82 | 530.39 | +0.65% |
| Fan B IGV FB | 102.00 | 100.52 | +1.47% |
| A/B Current Imbalance | -47.06% | baseline -47.21% ± 0.62% | — |

### IGV feedback abnormal for RPM/demand

2024-05-15 07:05:00 — Load 103.2% MCR

> Control-position or feedback relationship has changed. > > Required confirmation (doc, unmodified): Verify command vs feedback, linkage/actuator condition and operating mode.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A RPM | 1169.26 | 1167.63 | +0.14% |
| Fan A Current | 324.85 | 326.96 | -0.65% |
| Fan A IGV FB | 101.00 | 100.47 | +0.52% |
| Fan B RPM | 1175.32 | 1171.24 | +0.35% |
| Fan B Current | 527.83 | 530.39 | -0.48% |
| Fan B IGV FB | 102.00 | 100.52 | +1.47% |
| A/B Current Imbalance | -47.61% | baseline -47.21% ± 0.62% | — |

### A/B residual divergence

2024-01-25 18:30:00 — Load 92.2% MCR

> One fan behaves differently from its own baseline or companion fan. > > Required confirmation (doc, unmodified): Confirm equal duty and compare downstream A/B air conditions.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A RPM | 1170.97 | 1180.30 | -0.79% |
| Fan A Current | 330.58 | 332.61 | -0.61% |
| Fan A IGV FB | 100.00 | 100.47 | -0.46% |
| Fan B RPM | 1177.87 | 1184.63 | -0.57% |
| Fan B Current | 542.36 | 537.19 | +0.96% |
| Fan B IGV FB | — | — | missing data |
| A/B Current Imbalance | -48.52% | baseline -47.21% ± 0.62% | — |

### All fan variables shift with load reference mismatch

2024-04-16 12:45:00 — Load 105.9% MCR

> Demand input may be unreliable or operation is transient, or a Fan deterioration issue requiring investigation. > > Required confirmation (doc, unmodified): Validate load and steam-flow relationship before fan diagnosis.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A RPM | 1198.95 | 1146.54 | +4.57% |
| Fan A Current | 332.40 | 317.18 | +4.80% |
| Fan A IGV FB | 101.00 | 100.40 | +0.60% |
| Fan B RPM | 1205.26 | 1152.05 | +4.62% |
| Fan B Current | 538.55 | 513.50 | +4.88% |
| Fan B IGV FB | 102.00 | 100.52 | +1.47% |
| A/B Current Imbalance | -47.34% | baseline -47.21% ± 0.62% | — |

### Multiple fan residuals persist with process deviation

2024-03-21 07:55:00 — Load 87.7% MCR

> Higher-confidence fan/system performance issue. > > Required confirmation (doc, unmodified): Escalate for cross-cluster and field verification.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A RPM | 997.65 | 1146.54 | -12.99% |
| Fan A Current | 157.28 | 317.18 | -50.41% |
| Fan A IGV FB | 0.00 | 100.44 | -100.00% |
| Fan B RPM | 1289.77 | 1152.05 | +11.95% |
| Fan B Current | 854.01 | 513.50 | +66.31% |
| Fan B IGV FB | 102.00 | 100.53 | +1.46% |
| A/B Current Imbalance | -137.79% | baseline -47.21% ± 0.62% | — |

## 5. Fan B IGV — investigated finding, not taken at face value

Fan B IGV's outlier rate in section 3 is high. Investigated before writing it up, same discipline as Cluster 1's stale-threshold finding — this is NOT simply "Fan B's IGV control is unhealthy 58% of the time."

Root cause, evidenced:

1. Training-side: the shared shared/data_quality.py stale-streak exclusion (same detector Cluster 1 already uses, same TRAINING_STALE_STREAK_ROWS=12 threshold that was originally calibrated for STACK_TEMPERATURE/FEGT's whole-degree quantization) excludes 17,829/18,279 (97.5%) of Fan A's and 15,321/18,279 (83.8%) of Fan B's IGV-FB training rows — because both fans' IGV feedback sits perfectly constant for weeks at a time (a genuine control characteristic, not a sensor fault), tripping the same "frozen value" rule. This leaves a thin, non-uniformly-distributed training sample.

2. Test-side: Fan B's IGV FB is a coarse, whole-integer-percent signal that makes discrete MONTHLY STEP CHANGES, not continuous variation:

| month | mean | std | n |
| --- | --- | --- | --- |
| 1 | nan | nan | 0 |
| 2 | 101.96 | 1.93 | 5,306 |
| 3 | 102.00 | 0.00 | 7,142 |
| 4 | 102.00 | 0.00 | 6,912 |
| 5 | 102.00 | 0.00 | 7,142 |
| 7 | 100.74 | 0.42 | 7,142 |
| 8 | 101.00 | 0.00 | 7,142 |
| 9 | 101.00 | 0.00 | 6,911 |
| 10 | 101.00 | 0.00 | 7,142 |
| 11 | 100.38 | 0.48 | 6,851 |
| 12 | 100.69 | 0.45 | 7,142 |

(month 1 has 0 rows in the test window for this column — it falls inside the confirmed 2024-01-18 to 2024-02-11 null gap, see cluster2_config.yaml's PA_FAN_B_IGV_FB note.)

Flow does not correlate with these month-to-month steps (same reason Load doesn't explain Flow, section 1.3), so a Flow-binned baseline — trained on a thin, quality-filtered slice that likely reflects only 1-2 of these months — does not generalize to the other months' different discrete IGV settings. The result is a real, evidenced high outlier rate, but its cause is a baseline-generalization limitation (thin/unrepresentative training data for a step-changing signal), not necessarily 58% of the year showing genuine IGV control abnormality. Flagged as a known limitation (section 6), not silently corrected — a time-aware (monthly or seasonal) baseline dimension, analogous to Cluster 1's own monthly-stratification fix for SA/TA seasonal drift, is the most likely real fix, left for a future revision.

## 6. Open items for Punarbasu / Awes

Doc's own two queries — already on the consolidated cross-module list (Module 2/PAI-S02 raised the same coal-composition/fuel-quality dependency question; not asked twice here, just noted as overlapping):

"If due to fuel change, if the air supply is more than usual needed for the same load how alert will be reliable for high RPM." (doc section 2)

"Fuel GCV also be the reference [variable]?" (doc section 2, Boiler Demand and Required Fan Duty)

New items from this cluster's own build:

PA Fan Head: confirm no real per-fan tag exists anywhere else in the historian (checked exhaustively this pass, found none) and/or confirm whether PA PR AT AIR BOX A/B is a valid Head substitute for Fan A/B respectively (see section 1.1) — resolving this re-enables the doc's full 3-input formula.

A/B Current structural offset: why do Fan A and Fan B draw ~47% different current at matched RPM and comparable Flow (section 1.5)? Different motor/fan capacity rating, or different current-transformer scaling between the two fans' instrumentation? Affects whether the learned -47% baseline is "normal for these two different fans" or masks a genuine, permanent imbalance that's simply never been absent from the data to compare against.

PA PR AT AIR BOX C: no confirmed correspondence to either fan at all — what is this third zone/point?

## 7. Known limitations — not implemented in this phase

Persistence / alarm timing not implemented. The doc explicitly wants alarm logic to combine "residual magnitude, persistence, data quality and supporting variables rather than trigger on a single instantaneous excursion," and imbalance flagged "for a specified persistence time." This report scores each row independently — no rolling-persistence state machine. persistence.minutes in cluster2_config.yaml is a placeholder for a future revision, same scope limitation Cluster 1's report already carries for its own A/B trend-analysis gap.

Cross-cluster confirmation is out of scope. The doc's own "Model boundary" note and Validation Framework's "Cross-cluster" row both expect PA pressure/flow, draft, and downstream air-distribution evidence from Clusters 3/5/8/11 to confirm an abnormal fan residual. None of those clusters exist yet — every required_confirmation string in this report is the doc's own text, unmodified; this validator does not attempt that confirmation itself.

Fan B IGV's high outlier rate is a baseline-generalization artifact on a thin, quality-filtered training sample for a step-changing signal, not a confirmed real control-health finding — see section 5. Believed fixable with a time-aware baseline dimension in a future revision, not attempted this pass.

Quantile-based Flow bins, band_width_std, comparable-duty tolerance, and the fan-running RPM threshold are all configurable defaults or empirically-chosen values, not doc-specified numbers (only the four calculated-indicator formulas and the A/B-comparability guard's existence are doc-verbatim) — see clusters/cluster2_config.yaml for every tunable field and its rationale.

Single fan-configuration baseline only (both-running) — correct for this plant's actual 2024 operating history (section 1.4), but means the one real Fan-A-stop event has no dedicated baseline to be scored against; it correctly shows as unknown/large-residual rather than being forced through the both-running model.

Not wired into `server.py` or the frontend — by design, per this phase's scope, same as Cluster 1.

## 8. Conclusion

Cluster 2 provides a Flow-referenced (not demand/Load-referenced, see section 1.3) normal-behaviour model for PA Fan-A and PA Fan-B control/electrical response, scored against a STEADY-state, fan-running-only, monthly-stratified baseline never exposed to the 73,427-row test window it's scored against. Across all 8 relationships, 88.8% of (relationship x row) combinations score consistent. All six of the doc's own residual-interpretation patterns (section 6 of the doc) genuinely occur in this plant's real 2024 data, including a coherent, physically-sensible real event (2024-03-21: Fan A stopping while Fan B's RPM/current visibly ramp up to compensate — see section 4's "Multiple fan residuals" example).

Stated plainly: because Head is unavailable and Load doesn't explain Flow here, every "consistent"/"outlier" result above answers whether a fan's RPM/Current/IGV is internally consistent with its own measured Flow — not whether the fan is correctly responding to boiler demand, which is what the doc's original f(Fan Flow, Fan Head, Steam Flow) framing implied. Both are legitimate, useful questions, but they are not the same question, and a consistent result here does not confirm the fan is tracking demand correctly — only that it's behaving as its own history at this Flow would predict.

The most consequential finding from building this cluster wasn't a fan health signal — it was two places where applying the doc's methodology literally, without checking real data first, would have produced a broken or misleading model: Load does not explain Fan Flow in this plant's real 2024 operating envelope (section 1.3), and the doc's own A/B imbalance formula would flag nearly every healthy row as an outlier without a learned, non-zero baseline (section 1.5). Root-cause assignment for any flagged pattern still requires the data-quality, operating-state, PA pressure/flow, and maintenance evidence the doc itself calls for — this cluster flags deterioration or control inconsistency early; it does not diagnose it alone.