# Cluster 4 — SA Fan Performance — Validation Report

Source: backend/clusters/docs/Cluster_4_SA_Fan_Performance_Technical_Note Final.docx Data: data/raw/boiler9_cleaned_2024.csv, 91,767 rows, 2024-01-18 00:00:00 to 2024-12-31 23:55:00

Standalone offline pipeline, same phased methodology as Cluster 1/2 — read the doc, verify real tag availability (Step 0), build config -> baseline -> validator (Steps 1-3), produce this report (Step 4). Not wired into any live module or dashboard — by design, same scope limitation as Cluster 1/2.

Structurally the SA mirror of Cluster 2 (PA Fan Performance) — same code pattern reused directly — but NONE of Cluster 2's specific empirical findings were assumed to carry over. Every one was independently re-checked against SA's own real data; several came out differently (see section 1).

Read this before the numbers below: unlike PA, SA Fan Head is genuinely usable (kept in the model, stratify_by: [FLOW, HEAD]) — but SA has no control-position/IGV-equivalent tag at all (confirmed absent, not differently-named). The fan_igv relationship is therefore never computed for either fan (always unknown) — this model answers "is each fan's Speed/Current internally consistent with its own measured Flow and Head?", with no IGV-based diagnostic at all, a narrower set of relationships than either the doc's original 3-variable framing or Cluster 2's PA model.

## 1. Methodology

### 1.1 Doc artifacts (not technical findings)

The source .docx is a copy of Cluster 2's PA note with an incomplete find/replace: the title still says "Cluster 2 - SA Fan Performance" (wrong cluster number), and three places still say "PA"/"PA-system" where SA was clearly intended (Table 5's "Model boundary", Table 6's cross-cluster row, Table 7's RPM-high interpretation). Table 1 (the actual variable/tag table) was correctly updated to SA throughout. Treated as SA everywhere here per the doc's own stated intent (paragraph 3: "Cluster 4 groups each Secondary Air (SA) fan's...") — not a decision, just noting the artifact.

### 1.2 SA Fan Head — usable, unlike PA (Step 0 finding)

SA PR TO APH(A) and SA PR TO APH(B) are confirmed genuinely distinct — pandas.Series.equals() returns False (NOT a duplicate like PA's single "PA PR TO HGG"/"PA PR TO APH (A)" pair). Real per-fan data. Caveat: the two are extremely highly correlated with each other (corr = 0.99996, means only ~1% apart: 550.6 vs 555.8) — real, but may not differentiate Fan A's vs Fan B's model much in practice. Kept in the model — no Head-drop decision needed here, unlike PA — stratify_by: [FLOW, HEAD] for all three relationships (2-dimensional quantile bins; cluster4_baseline.py reuses Cluster 2's binning code unchanged, since it was already written generically over however many stratify_by columns a relationship declares).

### 1.3 SA Fan Flow — available, simpler than PA, but with real nulls

SA FLOW- A / SA FLOW-B  are already single per-fan tags — no two-header average needed (unlike PA's PA FLOW TO HGG -A (1)/(2) pattern). Real data-quality gap PA's flow tags didn't have: 14,782 nulls (16.1%) for A, 13,683 (14.9%) for B. This flows through to the validator/baseline as ordinary missing-data handling, but is the main driver of this cluster's higher unknown/ambiguous rates versus Cluster 2's (see section 3) — not a new bug, a direct consequence of this tag's own null rate.

### 1.4 SA control position (IGV-equivalent) — confirmed absent

Searched IGV/damper/vane/guide/position/control/FB/feedback keywords across all 103 raw historian columns — zero SA-fan-specific hits. The only FB-suffixed tags are PA's own IGV FB pair and unrelated CV-116/121/104 FB control-valve tags (already investigated and rejected as an unclear spray-water-flow proxy elsewhere in this project). Decision (user, 2026-08-11): kept as a documented placeholder relationship (fan_igv.status: synthetic_needed in cluster4_config.yaml) rather than omitted from the config entirely, so the gap stays visible/auditable — cluster4_baseline.py/cluster4_validator.py both check each relationship's status and skip computation entirely for anything not available — no crash, no fabricated values. Consequently "IGV feedback abnormal for RPM/demand" (doc's residual-pattern table) can never fire here — see section 4.

### 1.5 Training / test split and filters

Same monthly-stratified 20/80 chronological split as Cluster 1/2 (shared/chronological_split.py).

Total rows: 91,767

Training window: 18,340 rows

STEADY-only (of training window): 18,279 rows ({'STEADY': 18279, 'LOW_LOAD': 61})

Fan-running-only (of STEADY training rows, per side — see 1.7): A: 18,279, B: 18,279

Test window (scored by the validator): 73,427 rows

Split diagnostics: 11 calendar months with data, 10 sampling gap(s) in the full dataset.

### 1.6 Flow-binned baseline, not Load-binned — checked fresh for SA, a materially different story than PA

corr(Load, SA Fan-A Flow) = 0.426, corr(Load, SA Fan-B Flow) = 0.422 — much stronger than PA's 0.11-0.14, so this was NOT dismissed on the correlation number alone the way PA's was.

Decomposed by time scale, because a real global correlation can still hide very different local behavior:

Correlation of monthly mean Load vs monthly mean Flow = 0.815 — a real, fairly strong seasonal/slow co-drift exists (e.g. January averages both lower load (95.4%) and lower flow (50.6 tph); March averages both higher load (103.3%) and higher flow (61.5 tph)).

Correlation after removing each month's own mean (within-month only) drops to 0.363 (r² ≈ 13%) — a real but moderate within-month relationship, not zero.

The range-restriction test pooled across the whole year (all months' rows binned together by raw Load %) comes back essentially flat: ratio 1.03 (within-bin std 103% of unconditional std). Pooling months this way is confounded, though — it doesn't mean no local relationship exists, only that this particular (month-blind) binning doesn't capture one.

Verified directly, not inferred: per-month correlation varies hugely — December ≈ -0.03, November ≈ 0.08, March = 0.17, but April = 0.60, May = 0.44, September = 0.44. The pooled 0.363 figure is an average across months with genuinely different coupling strength, not a uniform within-month relationship.

Re-running the SAME range-restriction test within a single month confirms this directly: within March (a weak month), 1-point Load bins give ratio 1.15 (no shrinkage, consistent with its weak 0.17 correlation). Within April (a strong month, r²=36%), the same bins give ratio 0.875 — real shrinkage, close to the theoretical value for a linear relationship of that strength (√(1-r²) = 0.80). So a within-month, narrow-Load-bin relationship genuinely DOES exist when a month has one — the flat pooled-across-months ratio reflects the pooling, not an absence of any real local relationship.

Same decision as PA (bin by Flow, not Load) reached here too, but for a materially different, now-verified reason: not "no relationship exists" (PA's finding, and not fully accurate for SA either) but "the coupling strength itself varies month to month, and this baseline's Flow-only, month-blind binning doesn't (yet) capture the within-month structure that's been shown to exist." A joint month+Flow (or month+Load) baseline dimension is a promising, now better-evidenced future improvement, not attempted this phase — same spirit as section 1.4's IGV gap and Cluster 2's own noted Fan-B-IGV limitation.

### 1.7 Fan-running derivation and fan-configuration mix — checked fresh for SA

No dedicated fan run/stop/trip tag exists for either fan (confirmed, same as PA). Derived from Speed (doc's own suggestion) — not PA's 500 RPM value copied over: SA Speed's 0.1th percentile sits at ~900-902, with counts below 500 and below 700 identical (37/37 rows), confirming a clean, wide gap independently of PA's. fan_running.rpm_threshold: 600 sits in that gap.

Fan-configuration mix: this plant runs BOTH SA fans essentially continuously through 2024, same conclusion as PA reached independently. Two real exceptions found — not the same event as PA's:

1. 2024-05-17, ~08:35-11:30 (~3 hrs) — Fan A drops to near-zero speed/current while Fan B stays steady (~207-211 A) — a genuine, coherent single-fan-stop event, SA-specific, a different date than PA's 2024-03-21 event.

2. 2024-02-11 13:30 — same timestamp as PA's and Cluster 1's already-known historian sampling-gap event (KNOWN_BAD_TIMESTAMPS) — a plant-wide logging hiccup, not an SA-specific finding.

No per-configuration baselines built, same reasoning as Cluster 2.

### 1.8 A/B imbalance baseline — checked fresh, same fix as PA needed, different magnitude

SA's own check (not assumed from PA's ~47% Current offset): Current imbalance mean +13.7% (IQR +11.9% to +16.2%, std 6.1 pts, full dataset) — smaller in magnitude than PA's, but still clearly non-zero; a fixed threshold at zero would still bias-flag most healthy rows. Speed imbalance, like PA's RPM imbalance, genuinely IS centered near zero (mean +0.03%, tight IQR). Both metrics get the SAME learned-STEADY-state-band treatment as Cluster 2 for architectural consistency (not special-casing Speed just because its offset happens to already be small).

### 1.9 Fan A Speed — same stale-exclusion mechanism as Cluster 2's IGV finding, checked explicitly, smaller and differently-shaped effect

Fan A's Speed tag repeats its exact previous reading in 61.6% of rows, versus 3.2% for Fan B. Checked explicitly whether this trips the same shared/data_quality.py stale-streak exclusion that thinned Cluster 2's Fan B IGV training data, rather than assuming it does or doesn't:

Confirmed yes, and isolated the cause: of Fan A's 18,279 running-STEADY training rows, 7,988 (43.7%) are excluded, and the exclusion is 100% attributable to the stale-streak detector (0 spikes, 0 known-bad-timestamps, checked separately) — the identical mechanism as Cluster 2's case. Fan B's equivalent exclusion is only 146 rows (0.8%).

Checked whether this produces the same generalization failure: Fan A's test-window RPM outlier rate (13.6% overall) is meaningfully higher than Fan B's (7.9%), worst in July (40.2% vs 14.2%) — a real, month-varying degradation in the same direction as Cluster 2's finding, not just a training-side statistic with no downstream effect.

But the underlying character is different, checked via the actual repeat-run-length distribution (not assumed identical to Cluster 2's case): median run length is 1 (no repeat at all), only 2.75% of runs reach the 12-row exclusion threshold, and the longest runs reach up to 697 rows (~58 hours). This is a heterogeneous mix of brief repeats plus occasional long holds — not Cluster 2's clean "constant for entire calendar months" pattern (which showed literal std=0 for full months at a time). Consistent with a coarser logging resolution or intermittent hold behavior on this specific tag, not a sensor fault, and a real but smaller-magnitude version of Cluster 2's finding (13.6% overall outlier rate here vs Cluster 2's 58.2% for Fan B IGV) — flagged with the same rigor, not assumed to be identical just because the mechanism matches (section 6).

## 2. Parameters, thresholds and tolerances (all user-configurable)

Per the doc's own instruction — "Absolute limits should be finalized from approved design data and reviewed healthy operation; they should not be assumed from generic fan behavior" — every number below is a reasonable configurable default pending plant validation, not a doc-given value (only the formulas themselves, doc Table 2/4, are used verbatim).

| Setting | Value | Source |
| --- | --- | --- |
| fan_rpm.status | available | Step 0/1 finding, see section 1 |
| fan_rpm.band_width_std | 2.0 | configurable default |
| fan_rpm.stratify_by | ['FLOW', 'HEAD'] | Step 0/1 decision, see 1.2/1.6 |
| fan_rpm.n_bins | 5 | configurable default |
| fan_igv.status | synthetic_needed | Step 0/1 finding, see section 1 |
| fan_igv.band_width_std | 2.0 | configurable default |
| fan_igv.stratify_by | ['FLOW', 'HEAD'] | Step 0/1 decision, see 1.2/1.6 |
| fan_igv.n_bins | 5 | configurable default |
| fan_current.status | available | Step 0/1 finding, see section 1 |
| fan_current.band_width_std | 2.0 | configurable default |
| fan_current.stratify_by | ['FLOW', 'HEAD'] | Step 0/1 decision, see 1.2/1.6 |
| fan_current.n_bins | 5 | configurable default |
| ab_imbalance_guard.comparable_duty_tolerance_pct | 15.0 | configurable default |
| ab_imbalance_guard.band_width_std | 2.0 | configurable default |
| fan_running.rpm_threshold | 600.0 RPM | empirically chosen for SA, see 1.7 |
| baseline.min_samples | 20 | configurable default, same as Cluster 1/2 |
| persistence.minutes | 15 | configurable default — not implemented this phase, see section 7 |

## 3. Summary status by relationship

Scored across the full test window (73,427 rows, unseen by training). fan_a_igv/fan_b_igv show 100% unknown by construction — no real tag exists for SA (section 1.4), not a scoring failure.

### fan_a_rpm

| status | rows | % |
| --- | --- | --- |
| consistent | 51,799 | 70.54% |
| outlier | 10,005 | 13.63% |
| unknown | 11,623 | 15.83% |

### fan_a_current

| status | rows | % |
| --- | --- | --- |
| consistent | 54,326 | 73.99% |
| outlier | 7,478 | 10.18% |
| unknown | 11,623 | 15.83% |

### fan_a_igv

| status | rows | % |
| --- | --- | --- |
| unknown | 73,427 | 100.00% |

### fan_b_rpm

| status | rows | % |
| --- | --- | --- |
| consistent | 56,582 | 77.06% |
| outlier | 5,793 | 7.89% |
| unknown | 11,052 | 15.05% |

### fan_b_current

| status | rows | % |
| --- | --- | --- |
| consistent | 57,667 | 78.54% |
| outlier | 4,708 | 6.41% |
| unknown | 11,052 | 15.05% |

### fan_b_igv

| status | rows | % |
| --- | --- | --- |
| unknown | 73,427 | 100.00% |

### ab_current_imbalance

| status | rows | % |
| --- | --- | --- |
| consistent | 60,796 | 82.80% |
| outlier | 972 | 1.32% |
| ambiguous | 11,659 | 15.88% |

### ab_rpm_imbalance

| status | rows | % |
| --- | --- | --- |
| consistent | 60,913 | 82.96% |
| outlier | 855 | 1.16% |
| ambiguous | 11,658 | 15.88% |
| unknown | 1 | 0.00% |

### Diagnostic pattern occurrence (doc section 6 table)

| pattern | rows |
| --- | --- |
| Current high; RPM and demand normal | 2,581 |
| RPM high for normal demand | 6,292 |
| IGV feedback abnormal for RPM/demand | 0 |
| A/B residual divergence | 1,018 |
| All fan variables shift with load reference mismatch | 5,201 |
| Multiple fan residuals persist with process deviation | 1,217 |
| (no flagged pattern — healthy) | 57,118 |

## 4. Worked examples — real cases per residual pattern

Per the brief: at least one real case per row of the doc's residual-interpretation table (section 6), pulled from this report's own test-window scoring — none forced. "IGV feedback abnormal for RPM/demand" cannot occur here (igv status is always unknown, never outlier — see section 1.4) and is reported honestly as absent, not omitted from this list.

### Current high; RPM and demand normal

2024-11-19 19:30:00 — Load 101.0% MCR

> Additional electrical/mechanical loading or current measurement issue. > > Required confirmation (doc, unmodified): Check persistence, A/B comparison, maintenance data and related pressures/flows.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A Speed | 1186.00 | 1168.92 | +1.46% |
| Fan A Current | 202.06 | 185.02 | +9.21% |
| Fan A IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| Fan B Speed | 1188.32 | 1191.73 | -0.29% |
| Fan B Current | 171.87 | 164.36 | +4.57% |
| Fan B IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| A/B Current Imbalance | 16.15% | baseline 13.06% ± 2.97% | — |

### RPM high for normal demand

2024-05-09 00:35:00 — Load 102.7% MCR

> More speed is required than the learned baseline. > > Required confirmation (doc, unmodified): Check SA-system resistance, air delivery and fan control state.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A Speed | 1218.76 | 1297.80 | -6.09% |
| Fan A Current | 192.41 | 196.00 | -1.83% |
| Fan A IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| Fan B Speed | 1214.87 | 1242.91 | -2.26% |
| Fan B Current | 171.41 | 176.19 | -2.71% |
| Fan B IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| A/B Current Imbalance | 11.55% | baseline 13.06% ± 2.97% | — |

### IGV feedback abnormal for RPM/demand

Did not occur in the 2024 test window — expected for the IGV pattern (section 1.4); genuinely absent, not a forced omission.

### A/B residual divergence

2024-04-22 00:10:00 — Load 100.2% MCR

> One fan behaves differently from its own baseline or companion fan. > > Required confirmation (doc, unmodified): Confirm equal duty and compare downstream A/B air conditions.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A Speed | 1189.00 | 1227.59 | -3.14% |
| Fan A Current | 180.54 | 196.00 | -7.89% |
| Fan A IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| Fan B Speed | 1199.51 | 1238.67 | -3.16% |
| Fan B Current | 168.39 | 176.49 | -4.59% |
| Fan B IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| A/B Current Imbalance | 6.96% | baseline 13.06% ± 2.97% | — |

### All fan variables shift with load reference mismatch

2024-07-24 11:45:00 — Load 99.1% MCR

> Demand input may be unreliable, or operation is transient or Fan deterioration issue requiring investigation. > > Required confirmation (doc, unmodified): Validate load and steam-flow relationship before fan diagnosis.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A Speed | 1278.93 | 1286.81 | -0.61% |
| Fan A Current | 214.20 | 227.04 | -5.66% |
| Fan A IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| Fan B Speed | 1268.75 | 1290.14 | -1.66% |
| Fan B Current | 185.17 | 193.31 | -4.21% |
| Fan B IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| A/B Current Imbalance | 14.54% | baseline 13.06% ± 2.97% | — |

### Multiple fan residuals persist with process deviation

2024-04-08 09:35:00 — Load 94.4% MCR

> Higher-confidence fan/system performance issue. > > Required confirmation (doc, unmodified): Escalate for cross-cluster and field verification.

| variable | actual | predicted | deviation % |
| --- | --- | --- | --- |
| Fan A Speed | 1006.00 | 1097.43 | -8.33% |
| Fan A Current | 148.43 | 170.52 | -12.95% |
| Fan A IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| Fan B Speed | 1006.28 | 1103.90 | -8.84% |
| Fan B Current | 135.02 | 152.74 | -11.61% |
| Fan B IGV FB | — | — | no real tag for this relationship -- see cluster4_config.yaml |
| A/B Current Imbalance | 9.47% | baseline 13.06% ± 2.97% | — |

## 5. Open items for Punarbasu / Awes

Doc's own two queries (Table 1 area, same wording pattern as Cluster 2's doc) — already on the consolidated cross-module list, not asked twice:

Fuel-change / air-supply-vs-alert-reliability question (same as Cluster 2/Module 2's coal-composition dependency question).

Whether Fuel GCV should also be a reference variable (same as Cluster 2's open item).

New items from this cluster's own build:

SA control-position/IGV-equivalent tag: confirmed absent across the whole historian (section 1.4) — is there really no damper/vane feedback signal logged for these fans, or does one exist under a name this search didn't anticipate? If genuinely absent, the fan_igv relationship stays permanently unscoreable, not just blocked pending a lab report.

SA Fan Head correlation: SA PR TO APH(A) and (B) correlate at 0.99996 with each other (section 1.2) — is this expected (a shared header/plenum both taps draw from) or does it suggest one of the two taps isn't measuring what its name implies?

A/B Current structural offset: why do SA Fan A and Fan B draw ~13.7% different current at comparable duty (section 1.8)? Smaller than PA's ~47% but same open question: different motor/fan rating, or different CT scaling?

Fan A Speed resolution: confirmed real (61.6% repeat-previous-value rate vs Fan B's 3.2%, section 1.9) — is Fan A's Speed tag logged at a coarser resolution or on a longer hold/deadband than Fan B's, by design?

## 6. Known limitations — not implemented in this phase

No IGV-based diagnostic exists for SA at all (section 1.4) — a structural gap, not an implementation gap; nothing to implement without a real tag.

Persistence / alarm timing not implemented. Same scope limitation as Cluster 1/2's reports — each row scored independently, no rolling- persistence state machine.

Cross-cluster confirmation is out of scope. Every required_confirmation string in this report is the doc's own text, unmodified; this validator does not attempt that confirmation itself. Same limitation as Cluster 2.

Fan A Speed's high training-exclusion rate (section 1.9) reflects a real, coarser logging resolution on that specific tag, not confirmed fan-health information — flagged rather than silently absorbed into the baseline without comment.

The baseline is Flow-only and month-blind, but Load-Flow coupling strength varies seasonally — the current baseline likely under-uses available predictive signal in strong-coupling months. Verified directly (section 1.6), not just inferred from the pooled correlation: per-month corr(Load, Flow) ranges from near-zero in weak months (December ≈ -0.03, March = 0.17) up to r² ≈ 36% in April (corr = 0.60), with May/September also fairly strong (~0.44 each). A within-month, narrow-Load-bin range-restriction test confirms this is a real, bin-level-usable relationship in strong months (April: within-bin std shrinks to 87.5% of unconditional, close to the theoretical 80% for that r²) and genuinely absent in weak ones (March: 115%, no shrinkage) — so this isn't just seasonal noise, it's a real signal the current model doesn't use. A future revision could add a monthly/seasonal stratification dimension to the baseline to capture this — the same general fix Cluster 1 already applied for its own SA/TA side-balance seasonal-drift finding (monthly-stratified training, see clusters/cluster_baseline.py's docstring), adapted here to a month-aware scoring dimension rather than just a month-aware training split. Not implemented this phase — documented here so it isn't silently lost, same treatment as Fan B IGV's limitation in Cluster 2 and the persistence/alarm-timing gap above.

Quantile-based Flow/Head bins, band_width_std, comparable-duty tolerance, and the fan-running Speed threshold are all configurable defaults or empirically-chosen values, not doc-specified numbers — see clusters/cluster4_config.yaml for every tunable field and its rationale.

Single fan-configuration baseline only (both-running) — correct for this plant's actual 2024 operating history (section 1.7).

Not wired into `server.py` or the frontend — by design, per this phase's scope, same as Cluster 1/2.

## 7. Conclusion

Cluster 4 provides a Flow+Head-referenced normal-behaviour model for SA Fan-A and SA Fan-B Speed/Current — narrower than the doc's original 3-variable framing (no IGV-equivalent tag exists for SA at all, section 1.4) and narrower than Cluster 2's PA model in that specific respect, but BROADER than PA's in another: Head is genuinely usable here (section 1.2), unlike PA's blocked case. Across the 6 relationships that can actually be scored (excluding the two permanently-unknown IGV columns — see section 3), 77.6% of (relationship x row) combinations score consistent across the 73,427-row test window.

Five of the doc's six residual-interpretation patterns genuinely occur in this plant's real 2024 data; the sixth ("IGV feedback abnormal for RPM/demand") cannot occur by construction and is reported as such, not omitted (section 4).

Not a copy of Cluster 2's conclusions: this cluster's decisions were each independently re-derived from SA's own data and came out genuinely different from PA's in several places — Head is usable here (PA: blocked), the Load-Flow relationship is real but seasonally-mediated here (PA: essentially absent), the A/B Current offset is ~14% here (PA: ~47%), and the fan-running/stop events are different dates entirely. The one consistent finding across both clusters is architectural, not numerical: applying either doc's formulas literally, without checking real data first, would have produced a misleading model in at least one place — for PA it was the Load-Flow assumption and the A/B imbalance zero-point; for SA it's the same two categories of finding, but with different magnitudes and a different root cause for the Load-Flow result. Root-cause assignment for any flagged pattern still requires the data-quality, operating-state, SA pressure/flow, and maintenance evidence the doc itself calls for — this cluster flags deterioration or control inconsistency early; it does not diagnose it alone.